## 00_说明与结论
10kV案例建模前期准备 V2 | 基于本轮“结构化档距段表 + 单线/接线图”重新梳理，不把旧拓扑假设直接带入。
核心结论1 | 结构化表只覆盖杆塔-档距段，开关、分支箱、开闭所等设备连接未完整入表；原始连通分量不能直接解释为真实电气孤岛。
核心结论2 | 六条目标馈线图纸中确认3条“墩集变↔河湾变”直接跨站联络：dnan↔hpao、dzhen↔hdong、dxi↔hpao。
核心结论3 | hdong↔hzhen为河湾变站内馈线联络；dxi↔dzhen还存在开闭所母联/双电源迹象。二者可用于馈线重构，但不应直接计作两座110kV站之间的新增互济通道。
核心结论4 | T01(dnan↔hpao)两侧从馈线源端到联络点的表格路径在基础开关修复后均可形成，最适合作为第一条“现有联络转供”基准案例。
核心结论5 | T02与T03各有一侧因表格遗漏支线挂接/分支箱链而不可直接寻路，必须先按图纸补成“开关层/虚拟设备层”。
长度质量提示 | 5条馈线所有档距均固定50m；hzhen为50/60m两档。应视为名义/标准化档距，可用于第一版现有线路阻抗近似，但不能拿来估算新建线路的地理路径和造价。
推荐建模数据结构 | Layer 1 物理档距边（杆塔/长度/导线） + Layer 2 开关设备边（开关/分支箱/开闭所/母联/状态） → 按常态开合状态生成 operational graph。
第一阶段案例边界 | 先做3条跨站直接联络的正常/故障转供能力；同站联络作为站内重构辅助；外部馈线只保留边界节点，不展开。
P0门槛 | 开关常态状态、遗漏设备挂接、导线R/X/载流量、10kV负荷分布、110kV源端可用裕度、运行约束。P0未闭环前不进入正式潮流/优化结果。

## 01_馈线概览
别名 | 中文名 | 馈线编号 | 110kV站 | 建议源端根节点 | 原始档距段数 | 原始节点数 | 原始连通分量数 | 分量规模 | 名义总长度(km) | 档距模式 | 导线型号分布 | 目标联络数 | 其中跨站联络数 | 当前可建模性判断
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线01杆 | 267 | 269 | 2 | 263,6 | 13.35 | 50m×267 | JKLYJ/Q-10-240×267 | 1 | 1 | 主干+T01侧基本可用；黄安七支站等支线仍需挂接修复
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线01杆 | 161 | 167 | 6 | 69,55,26,12,3,2 | 8.05 | 50m×161 | JKLYJ/Q-10-240×145; JKLGYJ-70×12; JKLYJ-240/10×3; JLRX/T-120/30×1 | 2 | 1 | 主干开关缺口可修；T02王场湖支线挂接是关键P0缺口
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线01杆 | 191 | 193 | 2 | 148,45 | 9.55 | 50m×191 | JKLYJ/Q-10-240×191 | 2 | 1 | 补23/24开关后原始网络可合并；T03的本侧路径可用
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线1杆 | 195 | 202 | 7 | 90,47,27,14,12,10,2 | 9.75 | 50m×195 | JKLGYJ-240×155; JL(GD)/GIA-240/40×39; JLB3-35×1 | 2 | 1 | 多处开关/顺序缺口；按图纸修复后可合并，T02/T04侧均可用
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线01杆 | 72 | 78 | 6 | 36,21,11,6,2,2 | 3.6 | 50m×72 | LGJ-10-240×55; JKLYJ-150×6; JL/G1A-240/30×6; JKLYJ/QN-10-240×5 | 2 | 2 | 主干开关可修；T03王场湖支线需补分支箱/开关链
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线01#杆 | 238 | 240 | 2 | 135,105 | 13.79 | 50m×49; 60m×189 | JKLYJ/Q-10-240×238 | 1 | 0 | 补73/74开关后可合并；T04侧可用

## 02_联络关系
联络ID | 类型 | 站间关系 | A侧站 | A别名 | A馈线 | A端点 | B侧站 | B别名 | B馈线 | B端点 | 图纸证据 | 常态状态 | 三遥 | 建模处理/前置条件 | 优先级
T01 | 直接联络开关 | 跨站 | 墩集变 | dnan | 墩南线 | dnan线合金厂支线4杆 | 河湾变 | hpao | 河炮线 | hpao线59杆 | 图纸：dnan线合金厂支线4 与 hpao线59 联络开关 | 未可靠判定 | 否 | 两侧主干路径在现有表+基础修复后均可达；最适合优先做基准联络案例 | A
T02 | 直接联络开关 | 跨站 | 墩集变 | dzhen | 墩振线 | 王场湖支线17杆 | 河湾变 | hdong | 河东线 | hdong线93杆 | 图纸：hdong线93 与 dzhen线王场湖支线17 联络开关 | 未可靠判定 | 否 | hdong侧可达；dzhen侧王场湖支线父挂接缺失，须先修复R005 | B
T03 | 直接联络开关 | 跨站 | 墩集变 | dxi | 墩西线 | dxi线王场湖支线14 | 河湾变 | hpao | 河炮线 | hpao线王场湖支线1杆 | 图纸：hpao线王场湖1 与 dxi线王场湖14 联络开关（三遥） | 未可靠判定 | 是 | dxi侧可达；hpao侧需补分支箱/开关链R020 | B
T04 | 直接联络开关 | 同站 | 河湾变 | hdong | 河东线 | hdong线48杆（raw:河镇线hdong48杆） | 河湾变 | hzhen | 河镇线 | 10kVhzhen线49#杆 | 图纸：hdong线48 与 hzhen线49 联络开关（三遥） | 未可靠判定 | 是 | 用于河湾变站内馈线重构，不计作墩集↔河湾跨站供电通道 | A
T05 | 开闭所母联/双电源 | 同站 | 墩集变 | dxi | 墩西线 | 开闭所接入点待映射 | 墩集变 | dzhen | 墩振线 | 开闭所接入点待映射 | 图纸：炮车邳州智能制造产业园开闭所内见dxidzhi线、dzhendzhi线及100A母联/1002隔离开关 | 未可靠判定 | 待核 | 建议作为二阶段精细化开关站模型；当前结构化表无法直接映射端点 | C

## 03_源端到联络点路径
路径ID | 联络ID | 馈线别名 | 源端 | 联络端点 | 名义路径长度(m) | 图边数 | 当前可达性 | 说明
P01 | T01 | dnan | dnan线01杆 | dnan线合金厂支线4杆 | 2250 | 45 | 可达 | 基于档距段名义长度；开关边按0长度拓扑边处理
P02 | T01 | hpao | hpao线01杆 | hpao线59杆 | 2750 | 58 | 可达 | 补主干开关连接R016~R018后可达
P03 | T02 | hdong | hdong线1杆 | hdong线93杆 | 4350 | 92 | 可达 | 补hdong主干缺口后可达
P04 | T02 | dzhen | dzhen线01杆 | 王场湖支线17杆 |  |  | 不可达 | 王场湖支线父挂接缺失R005；图纸补齐后再算路径
P05 | T03 | dxi | dxi线01杆 | dxi线王场湖支线14 | 3250 | 65 | 可达 | 补dxi 23/24开关边R009后可达
P06 | T03 | hpao | hpao线01杆 | hpao线王场湖支线1杆 |  |  | 不可达 | 需补王场湖支线分支箱/开关链R020
P07 | T04 | hdong | hdong线1杆 | hdong线48杆 | 2150 | 47 | 可达 | raw节点名需canonical映射
P08 | T04 | hzhen | 10kVhzhen线01#杆 | 10kVhzhen线49#杆 | 2880 | 48 | 可达 | 补73/74开关与否不影响49点路径

## 04_拓扑修复清单
修复ID | 别名 | 馈线 | 问题类型 | 端点/对象A | 端点/对象B | 证据 | 建议处理 | 优先级 | 状态
R001 | dnan | 墩南线 | 顺序档距缺口 | dnan线82杆 | dnan线83杆 | 图/表需复核 | 两端仍在同一大连通分量，可能存在替代路径；不可盲补50m线路 | P1 | 待核
R002 | dnan | 墩南线 | 支线档距缺口 | dnan线黄安六支站支线09杆 | dnan线黄安六支站支线10杆 | 表格顺序命名 | 疑似缺档距段；先核图纸连接和设备类型 | P1 | 待核
R003 | dnan | 墩南线 | 支线挂接缺失 | dnan线黄安七支站支线01杆 | 上级主干/分支点待定 | 表格形成6节点独立分量 | 需从图纸确定黄安七支站支线的实际挂接点 | P0 | 待补
R004 | dzhen | 墩振线 | 开关连接缺失 | dzhen线07杆 | dzhen线08杆 | 图纸存在dzhen线07开关 | 按开关元件连接，不新增50m档距 | P0 | 图纸已确认设备
R005 | dzhen | 墩振线 | 支线挂接缺失 | 污水厂/王场湖支线分量 | 上级主干/分支点待定 | 表格独立分量；包含王场湖支线17联络点 | 决定dzhen↔hdong联络路径是否可计算，必须从图纸补挂接 | P0 | 待补
R006 | dzhen | 墩振线 | 支线挂接缺失 | 正康/恒鼎分量 | 上级主干/分支点待定 | 表格独立分量 | 从图纸补支线父节点 | P1 | 待补
R007 | dzhen | 墩振线 | 支线挂接缺失 | 南方永磁分量 | 上级主干/分支点待定 | 表格独立3节点分量 | 从图纸补支线父节点 | P1 | 待补
R008 | dzhen | 墩振线 | 支线挂接缺失 | 北支线10~11杆分量 | 上级主干/分支点待定 | 表格独立2节点分量 | 从图纸补支线父节点 | P1 | 待补
R009 | dxi | 墩西线 | 开关连接缺失 | dxi线23杆 | dxi线24杆 | 图纸存在墩西线24开关 | 按开关元件连接；补后原始2个分量可合并 | P0 | 图纸已确认设备
R010 | hdong | 河东线 | 开关/连接缺失 | hdong线9杆 | hdong线10杆 | 表格顺序缺口 | 需结合图纸确认设备类型；先做拓扑修复候选 | P0 | 待核
R011 | hdong | 河东线 | 开关/连接缺失 | hdong线11杆 | hdong线12杆 | 表格顺序缺口 | 需结合图纸确认设备类型；先做拓扑修复候选 | P0 | 待核
R012 | hdong | 河东线 | 开关/连接缺失 | hdong线23杆 | hdong线24杆 | 表格顺序缺口 | 需结合图纸确认设备类型；先做拓扑修复候选 | P0 | 待核
R013 | hdong | 河东线 | 开关连接缺失 | hdong线41杆 | hdong线42杆 | 图纸41/42/43附近有开关；表中42写作“河镇线hdong42杆” | 建立raw→canonical映射，并按开关元件连接 | P0 | 图纸支持
R014 | hdong | 河东线 | 开关/连接缺失 | hdong线73杆 | hdong线74杆 | 图纸74附近有开关 | 按开关元件连接或核实具体端点 | P0 | 图纸支持
R015 | hdong | 河东线 | 支线档距缺失 | hdong线汇龙支线01杆 | hdong线汇龙支线02杆 | 表格形成独立分量 | 补该连接后可并入主网络；设备类型仍需图纸确认 | P1 | 待核
R016 | hpao | 河炮线 | 开关连接缺失 | hpao线36杆 | hpao线37杆 | 图纸存在hpao线36开关 | 按开关元件连接，不新增50m线路 | P0 | 图纸已确认设备
R017 | hpao | 河炮线 | 开关连接缺失 | hpao线42杆 | hpao线43杆 | 图纸存在hpao线42开关 | 按开关元件连接 | P0 | 图纸已确认设备
R018 | hpao | 河炮线 | 开关连接缺失 | hpao线43杆 | hpao线44杆 | 图纸存在hpao线43开关（三遥） | 按开关元件连接 | P0 | 图纸已确认设备
R019 | hpao | 河炮线 | 支线挂接缺失 | hpao线高坡塑料颗粒支线 | 上级主干/分支点待定 | 补主干开关后仍为11节点独立分量 | 从图纸补支线父节点 | P1 | 待补
R020 | hpao | 河炮线 | 开关设备链缺失 | hpao线王场湖支线1杆 | hpao主干43杆附近分支箱/开关链 | 图纸明确王场湖支线经分支箱/分支开关接入，表格却为2节点孤岛 | 需建立虚拟分支箱/开关节点；这是dxi↔hpao联络可计算的P0条件 | P0 | 图纸已确认结构
R021 | hzhen | 河镇线 | 开关连接缺失 | 10kVhzhen线73#杆 | 10kVhzhen线74杆 | 图纸存在hzhen线73开关 | 按开关元件连接；补后原始2个分量可合并 | P0 | 图纸已确认设备

## 05_外部边界联络
边界ID | 本侧别名 | 本侧馈线 | 本侧端点 | 外部馈线/端点 | 证据来源 | 处理建议
E01 | dnan | 墩南线 | dnan线73-11 | dzheng线50 | dnan图纸 | dzheng不应直接等同目标dzhen；目标墩振主线编号范围与50点不吻合，先按外部/歧义边界处理
E02 | dnan | 墩南线 | dnan线103 | dfan线pctqcbb支线16 | dnan图纸 | 外部馈线边界联络，当前六馈线模型不展开
E03 | dnan | 墩南线 | dnan恒鼎支线10 | dyang线01-1 | dnan图纸 | 外部馈线边界联络
E04 | dnan | 墩南线 | dnan线（具体端点需图纸定位） | dhong线军霞器材支线14 | dnan图纸 | 外部馈线边界联络
E05 | hdong | 河东线 | hdong线张村2变支线7-1 | mdong线张村支15 | hdong图纸 | 外部馈线边界联络
E06 | hzhen | 河镇线 | hzhen线张村1变支线38 | mdong线62 | hzhen图纸 | 外部馈线边界联络（三遥）

## 06_导线型号字典
原始设备型号 | 出现档距段数 | 标准化型号 | R(Ω/km) | X(Ω/km) | 允许电流(A) | 参数状态 | 备注
JKLYJ/Q-10-240 | 841 | JKLYJ/Q-10-240 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JKLGYJ-240 | 155 | JKLGYJ-240 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
LGJ-10-240 | 55 | LGJ-10-240 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JL(GD)/GIA-240/40 | 39 | JL(GD)/GIA-240/40 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JKLGYJ-70 | 12 | JKLGYJ-70 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JKLYJ-150 | 6 | JKLYJ-150 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JL/G1A-240/30 | 6 | JL/G1A-240/30 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JKLYJ/QN-10-240 | 5 | JKLYJ/QN-10-240 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JKLYJ-240/10 | 3 | JKLYJ-240/10 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JLB3-35 | 1 | JLB3-35 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数
JLRX/T-120/30 | 1 | JLRX/T-120/30 |  |  |  | 待查 | 需用可靠设计/厂家/标准数据；不可按名称猜参数

## 07_建模字段缺口
缺口ID | 类别 | 优先级 | 缺失字段/信息 | 为什么必须 | 建议补齐方式 | 当前状态
G01 | 拓扑 | P0 | 所有开关的常态开/合状态 | 决定基准运行拓扑、联络开关是否常开、故障转供操作序列 | 将此前开/关表与新图纸开关名称统一ID后合并 | 未并入本轮包
G02 | 拓扑 | P0 | 表格遗漏的开关/分支箱/开闭所连接关系 | 消除“假孤岛”，才能形成可运行网络 | 按R001~R021逐项修复；开关作为独立元件/零长度拓扑边，不伪造50m线路 | 部分已由图纸确认
G03 | 电气参数 | P0 | 11种导线型号的R/X与允许电流/热稳定限值 | 潮流、电压、线路瓶颈与可转供容量均依赖 | 建立型号字典并引用设计手册/厂家或国网参数 | 待补
G04 | 负荷 | P0 | 节点/配变/馈线负荷及分配关系 | 仅有线路拓扑无法做潮流和N-1转供 | 至少得到馈线峰荷+配变容量/负荷分配；更优为典型时序负荷 | 待补
G05 | 源端 | P0 | 110kV主变容量、运行方式、站内可用裕度/N-1容量 | 跨站互济上限首先受源端余量约束 | 与110kV站级模型现有数据统一 | 待与主模型对接
G06 | 运行约束 | P0 | 10kV电压允许范围、线路/开关设备容量、辐射运行约束 | 确定联络转供是否可行及最大转供值 | 形成统一约束参数表 | 待定
G07 | 地理/造价 | P1 | 新建联络候选的真实路径长度/GIS坐标 | 现有档距长度呈50/60m标准化，不能用于新线路路线造价 | 新线长度单独由GIS/CAD测距或甲方给候选路径长度 | 待补
G08 | 经济参数 | P1 | 新建10kV线路、开关/环网柜、改造费用及年化参数 | 用于比较“利用现有联络”与“新增联络”的经济性 | 成本参数与研究报告口径统一 | 待补
G09 | 场景 | P1 | 正常峰荷/低谷、高PV反送、N-1故障集合 | 案例需要覆盖双向潮流，不应只做单一峰荷 | 建立典型工况集，先静态多场景，再决定是否需要8760h | 待设计
G10 | 精细化 | P2 | 用户配电室母联、开闭所母联、三遥/非三遥操作约束 | 影响实际可操作性，但不必阻塞第一阶段跨站案例 | 第一阶段保留边界标签，第二阶段按必要性展开 | 可后置

## 08_边表_原始
馈线别名 | 中文名 | 馈线编号 | 110kV站 | 源表行号 | 档距段名称 | 起始杆塔 | 终止杆塔 | 导线长度(m) | 设备型号 | 来源文件
dnan | 墩南线 | PZXL-00092 | 墩集变 | 2 | dnan线10杆~dnan线10+1 | dnan线10杆 | dnan线10+1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 3 | dnan线18杆~dnan线19杆 | dnan线18杆 | dnan线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 4 | dnan线41杆~dnan线42杆 | dnan线41杆 | dnan线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 5 | 波士达支线1杆~波士达支线1-1杆 | 波士达支线1杆 | 波士达支线1-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 6 | dnan线60杆~dnan线61杆 | dnan线60杆 | dnan线61杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 7 | 波士达支线1杆~波士达支线2杆 | 波士达支线1杆 | 波士达支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 8 | dnan线40杆~dnan线41杆 | dnan线40杆 | dnan线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 9 | dnan线10杆~dnan线11杆 | dnan线10杆 | dnan线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 10 | dnan线14杆~dnan线15杆 | dnan线14杆 | dnan线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 11 | dnan线黄安六支站支线01杆~dnan线黄安六支站支线02杆 | dnan线黄安六支站支线01杆 | dnan线黄安六支站支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 12 | 刘一刀支线1~刘一刀支线2 | 刘一刀支线1 | 刘一刀支线2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 13 | dnan线92杆~dnan线93杆 | dnan线92杆 | dnan线93杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 14 | dnan线黄安六支站支线09杆~dnan线黄安六支站支线9-1杆 | dnan线黄安六支站支线09杆 | dnan线黄安六支站支线9-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 15 | dnan线95杆~dnan线96杆 | dnan线95杆 | dnan线96杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 16 | dnan线合金厂支线1杆~dnan线合金厂支线2杆 | dnan线合金厂支线1杆 | dnan线合金厂支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 17 | dnan线46杆~dnan线47杆 | dnan线46杆 | dnan线47杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 18 | dnan线47杆~dnan线48杆 | dnan线47杆 | dnan线48杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 19 | dnan线42杆~dnan线合金厂支线1杆 | dnan线42杆 | dnan线合金厂支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 20 | dnan线54杆~dnan线55杆 | dnan线54杆 | dnan线55杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 21 | dnan线43杆~dnan线44杆 | dnan线43杆 | dnan线44杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 22 | dnan线51杆~dnan线52杆 | dnan线51杆 | dnan线52杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 23 | dnan线53杆~dnan线54杆 | dnan线53杆 | dnan线54杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 24 | dnan线50杆~dnan线51杆 | dnan线50杆 | dnan线51杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 25 | dnan线44杆~dnan线45杆 | dnan线44杆 | dnan线45杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 26 | dnan线48杆~dnan线49杆 | dnan线48杆 | dnan线49杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 27 | dnan线49杆~dnan线50杆 | dnan线49杆 | dnan线50杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 28 | dnan线45杆~dnan线46杆 | dnan线45杆 | dnan线46杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 29 | dnan线55杆~dnan线56杆 | dnan线55杆 | dnan线56杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 30 | dnan线42杆~dnan线43杆 | dnan线42杆 | dnan线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 31 | dnan线52杆~dnan线53杆 | dnan线52杆 | dnan线53杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 32 | dnan线08杆~dnan线09杆 | dnan线08杆 | dnan线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 33 | dnan线恒鼎支线25杆~dnan线恒鼎支线26杆 | dnan线恒鼎支线25杆 | dnan线恒鼎支线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 34 | dnan线18杆~dnan线恒鼎支线01杆 | dnan线18杆 | dnan线恒鼎支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 35 | dnan线恒鼎支线48杆~dnan线恒鼎支线49杆 | dnan线恒鼎支线48杆 | dnan线恒鼎支线49杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 36 | dnan线01杆~dnan线02杆 | dnan线01杆 | dnan线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 37 | dnan线35杆~dnan线36杆 | dnan线35杆 | dnan线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 38 | dnan线28杆~dnan线29杆 | dnan线28杆 | dnan线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 39 | dnan线98杆~dnan线99杆 | dnan线98杆 | dnan线99杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 40 | dnan线62杆~dnan线63杆 | dnan线62杆 | dnan线63杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 41 | dnan线23杆~dnan线24杆 | dnan线23杆 | dnan线24杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 42 | dnan线15杆~dnan线16杆 | dnan线15杆 | dnan线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 43 | dnan线96杆~dnan线97杆 | dnan线96杆 | dnan线97杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 44 | dnan线黄安七支站支线02杆~dnan线黄安七支站支线03杆 | dnan线黄安七支站支线02杆 | dnan线黄安七支站支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 45 | dnan线黄安七支站支线05杆~dnan线黄安七支站支线06杆 | dnan线黄安七支站支线05杆 | dnan线黄安七支站支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 46 | dnan线黄安六支站支线11~dnan线黄安六支站支线12 | dnan线黄安六支站支线11 | dnan线黄安六支站支线12 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 47 | dnan线天齐七支站支线02杆~dnan线天齐七支站支线03杆 | dnan线天齐七支站支线02杆 | dnan线天齐七支站支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 48 | dnan线13杆~dnan线14杆 | dnan线13杆 | dnan线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 49 | dnan线09杆~dnan线10杆 | dnan线09杆 | dnan线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 50 | dnan线93杆~dnan线94杆 | dnan线93杆 | dnan线94杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 51 | dnan线天齐七支站支线07杆~dnan线天齐七支站支线08杆 | dnan线天齐七支站支线07杆 | dnan线天齐七支站支线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 52 | dji南台支线10杆~dji南台支线11杆 | dji南台支线10杆 | dji南台支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 53 | dnan线97杆~dnan线98杆 | dnan线97杆 | dnan线98杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 54 | dji南台支线9杆~dji南台支线10杆 | dji南台支线9杆 | dji南台支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 55 | dnan线90杆~dnan线天齐七支站支线01杆 | dnan线90杆 | dnan线天齐七支站支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 56 | dji南台支线14杆~dji南台支线15杆 | dji南台支线14杆 | dji南台支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 57 | dnan线12杆~dnan线13杆 | dnan线12杆 | dnan线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 58 | dnan线17杆~dnan线18杆 | dnan线17杆 | dnan线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 59 | dnan线黄安六支站支线05杆~dnan线黄安六支站支线06杆 | dnan线黄安六支站支线05杆 | dnan线黄安六支站支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 60 | dnan线19杆~dnan线20杆 | dnan线19杆 | dnan线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 61 | dnan线20杆~dnan线21杆 | dnan线20杆 | dnan线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 62 | dnan线黄安七支站支线03杆~dnan线黄安七支站支线04杆 | dnan线黄安七支站支线03杆 | dnan线黄安七支站支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 63 | dnan线黄安六支站支线06杆~dnan线黄安六支站支线07杆 | dnan线黄安六支站支线06杆 | dnan线黄安六支站支线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 64 | dji南台支线12杆~dji南台支线13杆 | dji南台支线12杆 | dji南台支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 65 | dnan线22杆~dnan线23杆 | dnan线22杆 | dnan线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 66 | dnan线94杆~dnan线95杆 | dnan线94杆 | dnan线95杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 67 | dnan线天齐七支站支线05杆~dnan线天齐七支站支线06杆 | dnan线天齐七支站支线05杆 | dnan线天齐七支站支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 68 | dnan线天齐七支站支线06杆~dnan线天齐七支站支线07杆 | dnan线天齐七支站支线06杆 | dnan线天齐七支站支线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 69 | dnan线天齐七支站支线08杆~dnan线天齐七支站支线09杆 | dnan线天齐七支站支线08杆 | dnan线天齐七支站支线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 70 | dnan线黄安六支站支线04杆~dnan线黄安六支站支线05杆 | dnan线黄安六支站支线04杆 | dnan线黄安六支站支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 71 | dnan线16杆~dnan线17杆 | dnan线16杆 | dnan线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 72 | dnan线黄安六支站支线03杆~dnan线黄安六支站支线04杆 | dnan线黄安六支站支线03杆 | dnan线黄安六支站支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 73 | dnan线黄安六支站支线12~dnan线黄安六支站支线13 | dnan线黄安六支站支线12 | dnan线黄安六支站支线13 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 74 | dnan线17杆~军霞器材支线1杆 | dnan线17杆 | 军霞器材支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 75 | dnan线11杆~dnan线12杆 | dnan线11杆 | dnan线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 76 | dnan线黄安六支站支线08杆~dnan线黄安六支站支线09杆 | dnan线黄安六支站支线08杆 | dnan线黄安六支站支线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 77 | dnan线91杆~dnan线92杆 | dnan线91杆 | dnan线92杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 78 | dnan线黄安六支站支线07杆~dnan线黄安六支站支线08杆 | dnan线黄安六支站支线07杆 | dnan线黄安六支站支线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 79 | dnan线黄安七支站支线01杆~dnan线黄安七支站支线02杆 | dnan线黄安七支站支线01杆 | dnan线黄安七支站支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 80 | dji南台支线11杆~dji南台支线12杆 | dji南台支线11杆 | dji南台支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 81 | dnan线黄安七支站支线04杆~dnan线黄安七支站支线05杆 | dnan线黄安七支站支线04杆 | dnan线黄安七支站支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 82 | dnan线28杆~dnan线黄安六支站支线01杆 | dnan线28杆 | dnan线黄安六支站支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 83 | dnan线黄安六支站支线9-1杆~dnan线黄安六支站支线10 | dnan线黄安六支站支线9-1杆 | dnan线黄安六支站支线10 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 84 | dnan线90杆~dnan线91杆 | dnan线90杆 | dnan线91杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 85 | dnan线天齐七支站支线04杆~dnan线天齐七支站支线05杆 | dnan线天齐七支站支线04杆 | dnan线天齐七支站支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 86 | dnan线21杆~dnan线22杆 | dnan线21杆 | dnan线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 87 | dnan线天齐七支站支线01杆~dnan线天齐七支站支线02杆 | dnan线天齐七支站支线01杆 | dnan线天齐七支站支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 88 | dnan线天齐七支站支线03杆~dnan线天齐七支站支线04杆 | dnan线天齐七支站支线03杆 | dnan线天齐七支站支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 89 | dji南台支线13杆~dji南台支线14杆 | dji南台支线13杆 | dji南台支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 90 | dnan线黄安六支站支线02杆~dnan线黄安六支站支线03杆 | dnan线黄安六支站支线02杆 | dnan线黄安六支站支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 91 | dnan线恒鼎支线42杆~dnan线恒鼎支线43杆 | dnan线恒鼎支线42杆 | dnan线恒鼎支线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 92 | dnan线恒鼎支线18杆~dnan线恒鼎支线19杆 | dnan线恒鼎支线18杆 | dnan线恒鼎支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 93 | dnan线恒鼎支线23杆~dnan线恒鼎支线24杆 | dnan线恒鼎支线23杆 | dnan线恒鼎支线24杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 94 | dnan线29杆~dnan线30杆 | dnan线29杆 | dnan线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 95 | dnan线恒鼎支线24杆~dnan线恒鼎支线25杆 | dnan线恒鼎支线24杆 | dnan线恒鼎支线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 96 | dnan线恒鼎支线41杆~dnan线恒鼎支线42杆 | dnan线恒鼎支线41杆 | dnan线恒鼎支线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 97 | dnan线56杆~dnan线57杆 | dnan线56杆 | dnan线57杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 98 | dnan线07杆~dnan线08杆 | dnan线07杆 | dnan线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 99 | dnan线63杆~dnan线64杆 | dnan线63杆 | dnan线64杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 100 | dnan线恒鼎支线45杆~dnan线恒鼎支线46杆 | dnan线恒鼎支线45杆 | dnan线恒鼎支线46杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 101 | dnan线恒鼎支线17杆~dnan线恒鼎支线18杆 | dnan线恒鼎支线17杆 | dnan线恒鼎支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 102 | dnan线70杆~dnan线71杆 | dnan线70杆 | dnan线71杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 103 | dnan线59杆~dnan线60杆 | dnan线59杆 | dnan线60杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 104 | dnan线恒鼎支线20杆~dnan线恒鼎支线21杆 | dnan线恒鼎支线20杆 | dnan线恒鼎支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 105 | dnan线34杆~dnan线35杆 | dnan线34杆 | dnan线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 106 | dnan线101杆~dnan线102杆 | dnan线101杆 | dnan线102杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 107 | dnan线32杆~dnan线33杆 | dnan线32杆 | dnan线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 108 | dnan线恒鼎支线05杆~dnan线恒鼎支线06杆 | dnan线恒鼎支线05杆 | dnan线恒鼎支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 109 | dnan线恒鼎支线08杆~dnan线恒鼎支线09杆 | dnan线恒鼎支线08杆 | dnan线恒鼎支线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 110 | dnan线102杆~dnan线103杆 | dnan线102杆 | dnan线103杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 111 | dnan线37杆~dnan线38杆 | dnan线37杆 | dnan线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 112 | dnan线恒鼎支线15杆~dnan线恒鼎支线16杆 | dnan线恒鼎支线15杆 | dnan线恒鼎支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 113 | dnan线57杆~dnan线58杆 | dnan线57杆 | dnan线58杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 114 | dnan线77杆~dnan线78杆 | dnan线77杆 | dnan线78杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 115 | dnan线30杆~dnan线31杆 | dnan线30杆 | dnan线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 116 | dnan线80杆~dnan线81杆 | dnan线80杆 | dnan线81杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 117 | dnan线恒鼎支线26杆~dnan线恒鼎支线27杆 | dnan线恒鼎支线26杆 | dnan线恒鼎支线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 118 | dnan线87杆~dnan线88杆 | dnan线87杆 | dnan线88杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 119 | dnan线恒鼎支线06杆~dnan线恒鼎支线07杆 | dnan线恒鼎支线06杆 | dnan线恒鼎支线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 120 | dnan线恒鼎支线39杆~dnan线恒鼎支线40杆 | dnan线恒鼎支线39杆 | dnan线恒鼎支线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 121 | dnan线83杆~dnan线84杆 | dnan线83杆 | dnan线84杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 122 | dnan线恒鼎支线28杆~dnan线恒鼎支线29杆 | dnan线恒鼎支线28杆 | dnan线恒鼎支线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 123 | dnan线64杆~dnan线65杆 | dnan线64杆 | dnan线65杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 124 | dnan线38杆~dnan线39杆 | dnan线38杆 | dnan线39杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 125 | dnan线05杆~dnan线06杆 | dnan线05杆 | dnan线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 126 | dnan线36杆~dnan线37杆 | dnan线36杆 | dnan线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 127 | dnan线74杆~dnan线75杆 | dnan线74杆 | dnan线75杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 128 | dnan线26杆~dnan线27杆 | dnan线26杆 | dnan线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 129 | dnan线71杆~dnan线72杆 | dnan线71杆 | dnan线72杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 130 | dnan线06杆~dnan线07杆 | dnan线06杆 | dnan线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 131 | dnan线恒鼎支线43杆~dnan线恒鼎支线44杆 | dnan线恒鼎支线43杆 | dnan线恒鼎支线44杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 132 | dnan线72杆~dnan线73杆 | dnan线72杆 | dnan线73杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 133 | dnan线61杆~dnan线62杆 | dnan线61杆 | dnan线62杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 134 | dnan线88杆~dnan线89杆 | dnan线88杆 | dnan线89杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 135 | dnan线恒鼎支线44杆~dnan线恒鼎支线45杆 | dnan线恒鼎支线44杆 | dnan线恒鼎支线45杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 136 | dnan线86杆~dnan线87杆 | dnan线86杆 | dnan线87杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 137 | dnan线恒鼎支线09杆~dnan线恒鼎支线10杆 | dnan线恒鼎支线09杆 | dnan线恒鼎支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 138 | dnan线恒鼎支线34杆~dnan线恒鼎支线35杆 | dnan线恒鼎支线34杆 | dnan线恒鼎支线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 139 | dnan线恒鼎支线22杆~dnan线恒鼎支线23杆 | dnan线恒鼎支线22杆 | dnan线恒鼎支线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 140 | dnan线84杆~dnan线85杆 | dnan线84杆 | dnan线85杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 141 | dnan线恒鼎支线35杆~dnan线恒鼎支线36杆 | dnan线恒鼎支线35杆 | dnan线恒鼎支线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 142 | dnan线恒鼎支线38杆~dnan线恒鼎支线39杆 | dnan线恒鼎支线38杆 | dnan线恒鼎支线39杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 143 | dnan线恒鼎支线36杆~dnan线恒鼎支线37杆 | dnan线恒鼎支线36杆 | dnan线恒鼎支线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 144 | dnan线78杆~dnan线79杆 | dnan线78杆 | dnan线79杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 145 | dnan线89杆~dnan线90杆 | dnan线89杆 | dnan线90杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 146 | dnan线恒鼎支线13杆~dnan线恒鼎支线14杆 | dnan线恒鼎支线13杆 | dnan线恒鼎支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 147 | dnan线85杆~dnan线86杆 | dnan线85杆 | dnan线86杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 148 | dnan线65杆~dnan线66杆 | dnan线65杆 | dnan线66杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 149 | dnan线58杆~dnan线59杆 | dnan线58杆 | dnan线59杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 150 | dnan线恒鼎支线33杆~dnan线恒鼎支线34杆 | dnan线恒鼎支线33杆 | dnan线恒鼎支线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 151 | dnan线黄安六支站支线10~dnan线黄安六支站支线11 | dnan线黄安六支站支线10 | dnan线黄安六支站支线11 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 152 | dnan线39杆~dnan线40杆 | dnan线39杆 | dnan线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 153 | dnan线69杆~dnan线70杆 | dnan线69杆 | dnan线70杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 154 | dnan线25杆~dnan线26杆 | dnan线25杆 | dnan线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 155 | dnan线27杆~dnan线28杆 | dnan线27杆 | dnan线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 156 | dnan线75杆~dnan线76杆 | dnan线75杆 | dnan线76杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 157 | dnan线03杆~dnan线04杆 | dnan线03杆 | dnan线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 158 | dnan线恒鼎支线10杆~dnan线恒鼎支线11杆 | dnan线恒鼎支线10杆 | dnan线恒鼎支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 159 | dnan线02杆~dnan线03杆 | dnan线02杆 | dnan线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 160 | dnan线恒鼎支线04杆~dnan线恒鼎支线05杆 | dnan线恒鼎支线04杆 | dnan线恒鼎支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 161 | dnan线恒鼎支线40杆~dnan线恒鼎支线41杆 | dnan线恒鼎支线40杆 | dnan线恒鼎支线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 162 | dnan线恒鼎支线14杆~dnan线恒鼎支线15杆 | dnan线恒鼎支线14杆 | dnan线恒鼎支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 163 | dnan线恒鼎支线32杆~dnan线恒鼎支线33杆 | dnan线恒鼎支线32杆 | dnan线恒鼎支线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 164 | dnan线76杆~dnan线77杆 | dnan线76杆 | dnan线77杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 165 | dnan线66杆~dnan线67杆 | dnan线66杆 | dnan线67杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 166 | dnan线04杆~dnan线05杆 | dnan线04杆 | dnan线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 167 | dnan线恒鼎支线02杆~dnan线恒鼎支线03杆 | dnan线恒鼎支线02杆 | dnan线恒鼎支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 168 | dnan线33杆~dnan线34杆 | dnan线33杆 | dnan线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 169 | dnan线99杆~dnan线100杆 | dnan线99杆 | dnan线100杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 170 | dnan线24杆~dnan线25杆 | dnan线24杆 | dnan线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 171 | dnan线恒鼎支线29杆~dnan线恒鼎支线30杆 | dnan线恒鼎支线29杆 | dnan线恒鼎支线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 172 | dnan线恒鼎支线12杆~dnan线恒鼎支线13杆 | dnan线恒鼎支线12杆 | dnan线恒鼎支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 173 | dnan线恒鼎支线11杆~dnan线恒鼎支线12杆 | dnan线恒鼎支线11杆 | dnan线恒鼎支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 174 | dnan线恒鼎支线47杆~dnan线恒鼎支线48杆 | dnan线恒鼎支线47杆 | dnan线恒鼎支线48杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 175 | dnan线恒鼎支线03杆~dnan线恒鼎支线04杆 | dnan线恒鼎支线03杆 | dnan线恒鼎支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 176 | dnan线恒鼎支线21杆~dnan线恒鼎支线22杆 | dnan线恒鼎支线21杆 | dnan线恒鼎支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 177 | dnan线恒鼎支线30杆~dnan线恒鼎支线31杆 | dnan线恒鼎支线30杆 | dnan线恒鼎支线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 178 | dnan线73杆~dnan线74杆 | dnan线73杆 | dnan线74杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 179 | dnan线恒鼎支线07杆~dnan线恒鼎支线08杆 | dnan线恒鼎支线07杆 | dnan线恒鼎支线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 180 | dnan线31杆~dnan线32杆 | dnan线31杆 | dnan线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 181 | dnan线恒鼎支线46杆~dnan线恒鼎支线47杆 | dnan线恒鼎支线46杆 | dnan线恒鼎支线47杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 182 | dnan线67杆~dnan线68杆 | dnan线67杆 | dnan线68杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 183 | dnan线79杆~dnan线80杆 | dnan线79杆 | dnan线80杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 184 | dnan线恒鼎支线16杆~dnan线恒鼎支线17杆 | dnan线恒鼎支线16杆 | dnan线恒鼎支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 185 | dnan线恒鼎支线19杆~dnan线恒鼎支线20杆 | dnan线恒鼎支线19杆 | dnan线恒鼎支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 186 | dnan线68杆~dnan线69杆 | dnan线68杆 | dnan线69杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 187 | dnan线恒鼎支线27杆~dnan线恒鼎支线28杆 | dnan线恒鼎支线27杆 | dnan线恒鼎支线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 188 | dnan线81杆~dnan线82杆 | dnan线81杆 | dnan线82杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 189 | dnan线恒鼎支线01杆~dnan线恒鼎支线02杆 | dnan线恒鼎支线01杆 | dnan线恒鼎支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 190 | dnan线恒鼎支线37杆~dnan线恒鼎支线38杆 | dnan线恒鼎支线37杆 | dnan线恒鼎支线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 191 | dnan线100杆~dnan线101杆 | dnan线100杆 | dnan线101杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 192 | dnan线恒鼎支线31杆~dnan线恒鼎支线32杆 | dnan线恒鼎支线31杆 | dnan线恒鼎支线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 193 | dnan线合金厂支线2杆~dnan线合金厂支线3杆 | dnan线合金厂支线2杆 | dnan线合金厂支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 194 | dnan线82-1~dji南台支线1杆 | dnan线82-1 | dji南台支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 195 | dji南台支线1杆~dji南台支线2杆 | dji南台支线1杆 | dji南台支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 196 | dji南台支线8杆~dji南台支线9杆 | dji南台支线8杆 | dji南台支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 197 | 波士达支线3杆~波士达支线4杆 | 波士达支线3杆 | 波士达支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 198 | dji南台支线6杆~dji南台支线7杆 | dji南台支线6杆 | dji南台支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 199 | dji南台支线4杆~dji南台支线5杆 | dji南台支线4杆 | dji南台支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 200 | dji南台支线5杆~dji南台支线6杆 | dji南台支线5杆 | dji南台支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 201 | dnan线82杆~dnan线82-1 | dnan线82杆 | dnan线82-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 202 | 波士达支线2杆~波士达支线3杆 | 波士达支线2杆 | 波士达支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 203 | dji南台支线7杆~dji南台支线8杆 | dji南台支线7杆 | dji南台支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 204 | dnan线合金厂支线3杆~dnan线合金厂支线4杆 | dnan线合金厂支线3杆 | dnan线合金厂支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 205 | dnan线82-1~dnan线83杆 | dnan线82-1 | dnan线83杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 206 | dji南台支线2杆~dji南台支线3杆 | dji南台支线2杆 | dji南台支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 207 | dnan线21杆~波士达支线1杆 | dnan线21杆 | 波士达支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 208 | dji南台支线3杆~dji南台支线4杆 | dji南台支线3杆 | dji南台支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 209 | dnan线73-4~dnan线73-5 | dnan线73-4 | dnan线73-5 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 210 | dnan线73-6~dnan线73-7 | dnan线73-6 | dnan线73-7 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 211 | dnan线73-3~dnan线73-4 | dnan线73-3 | dnan线73-4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 212 | dnan线73-7~dnan线73-8 | dnan线73-7 | dnan线73-8 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 213 | dnan线73-1~dnan线73-2 | dnan线73-1 | dnan线73-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 214 | dnan线73-10~dnan线73-11 | dnan线73-10 | dnan线73-11 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 215 | dnan线73杆~dnan线73-1 | dnan线73杆 | dnan线73-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 216 | dnan线73-5~dnan线73-6 | dnan线73-5 | dnan线73-6 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 217 | dnan线73-8~dnan线73-9 | dnan线73-8 | dnan线73-9 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 218 | dnan线73-9~dnan线73-10 | dnan线73-9 | dnan线73-10 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 219 | dnan线73-2~dnan线73-3 | dnan线73-2 | dnan线73-3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 220 | dnan线天齐七支站支线10~dnan线天齐七支站支线11 | dnan线天齐七支站支线10 | dnan线天齐七支站支线11 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 221 | dnan线天齐七支站支线09杆~金凤凰1 | dnan线天齐七支站支线09杆 | 金凤凰1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 222 | dnan线天齐七支站支线12~dnan线天齐七支站支线13 | dnan线天齐七支站支线12 | dnan线天齐七支站支线13 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 223 | dnan线天齐七支站支线09杆~dnan线天齐七支站支线10 | dnan线天齐七支站支线09杆 | dnan线天齐七支站支线10 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 224 | 金凤凰1~金凤凰2 | 金凤凰1 | 金凤凰2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 225 | dnan线天齐七支站支线11~dnan线天齐七支站支线12 | dnan线天齐七支站支线11 | dnan线天齐七支站支线12 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 226 | dnan线恒鼎支线35杆-4~dnan线恒鼎支线35杆-5 | dnan线恒鼎支线35杆-4 | dnan线恒鼎支线35杆-5 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 227 | dnan线恒鼎支线35杆-1~dnan线恒鼎支线35杆-2 | dnan线恒鼎支线35杆-1 | dnan线恒鼎支线35杆-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 228 | dnan线恒鼎支线35杆-8~dnan线恒鼎支线35杆-9 | dnan线恒鼎支线35杆-8 | dnan线恒鼎支线35杆-9 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 229 | 国成支线4~国成支线5 | 国成支线4 | 国成支线5 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 230 | dnan线恒鼎支线35杆-6~dnan线恒鼎支线35杆-7 | dnan线恒鼎支线35杆-6 | dnan线恒鼎支线35杆-7 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 231 | dnan线恒鼎支线35杆~dnan线恒鼎支线35杆-1 | dnan线恒鼎支线35杆 | dnan线恒鼎支线35杆-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 232 | dnan线恒鼎支线35杆-5~dnan线恒鼎支线35杆-6 | dnan线恒鼎支线35杆-5 | dnan线恒鼎支线35杆-6 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 233 | 国成支线1~国成支线2 | 国成支线1 | 国成支线2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 234 | dnan线26杆~国成支线1 | dnan线26杆 | 国成支线1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 235 | dnan线恒鼎支线35杆-7~dnan线恒鼎支线35杆-8 | dnan线恒鼎支线35杆-7 | dnan线恒鼎支线35杆-8 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 236 | 国成支线3~国成支线4 | 国成支线3 | 国成支线4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 237 | dnan线恒鼎支线35杆-2~dnan线恒鼎支线35杆-3 | dnan线恒鼎支线35杆-2 | dnan线恒鼎支线35杆-3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 238 | 国成支线2~国成支线3 | 国成支线2 | 国成支线3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 239 | dnan线恒鼎支线35杆-3~dnan线恒鼎支线35杆-4 | dnan线恒鼎支线35杆-3 | dnan线恒鼎支线35杆-4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 240 | dnan线46杆~dnan线46-1 | dnan线46杆 | dnan线46-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 241 | dnan线黄安六支站支线9-1杆~刘一刀支线1 | dnan线黄安六支站支线9-1杆 | 刘一刀支线1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 242 | dnan线46-1~dnan线46-2 | dnan线46-1 | dnan线46-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 243 | dnan线黄安六支站支线14~dnan线黄安六支站支线15 | dnan线黄安六支站支线14 | dnan线黄安六支站支线15 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 244 | 大晶支线2~大晶支线3 | 大晶支线2 | 大晶支线3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 245 | dnan线黄安六支站支线17~dnan线黄安六支站支线18 | dnan线黄安六支站支线17 | dnan线黄安六支站支线18 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 246 | 大晶支线1~大晶支线2 | 大晶支线1 | 大晶支线2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 247 | dnan线56-1~dnan线56-2 | dnan线56-1 | dnan线56-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 248 | dnan线56杆~dnan线56-1 | dnan线56杆 | dnan线56-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 249 | dnan线64杆~大晶支线1 | dnan线64杆 | 大晶支线1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 250 | 大晶支线3~大晶支线4 | 大晶支线3 | 大晶支线4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 251 | 军霞器材支线5~军霞器材支线6 | 军霞器材支线5 | 军霞器材支线6 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 252 | 军霞器材支线6~军霞器材支线7 | 军霞器材支线6 | 军霞器材支线7 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 253 | 军霞器材支线7~军霞器材支线8 | 军霞器材支线7 | 军霞器材支线8 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 254 | 军霞器材支线3~军霞器材支线4 | 军霞器材支线3 | 军霞器材支线4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 255 | 军霞器材支线4~军霞器材支线5 | 军霞器材支线4 | 军霞器材支线5 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 256 | 军霞器材支线2~军霞器材支线3 | 军霞器材支线2 | 军霞器材支线3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 257 | 军霞器材支线1杆~军霞器材支线2 | 军霞器材支线1杆 | 军霞器材支线2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 258 | dnan线黄安六支站支线16~dnan线黄安六支站支线17 | dnan线黄安六支站支线16 | dnan线黄安六支站支线17 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 259 | dnan线黄安六支站支线13~dnan线黄安六支站支线14 | dnan线黄安六支站支线13 | dnan线黄安六支站支线14 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 260 | dnan线黄安六支站支线15~dnan线黄安六支站支线16 | dnan线黄安六支站支线15 | dnan线黄安六支站支线16 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 261 | dnan线53-1~dnan线53-2 | dnan线53-1 | dnan线53-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 262 | dnan线53-2~dnan线53-3 | dnan线53-2 | dnan线53-3 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 263 | dnan线53-5~dnan线53-6 | dnan线53-5 | dnan线53-6 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 264 | dnan线53杆~dnan线53-1 | dnan线53杆 | dnan线53-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 265 | dnan线53-3~dnan线53-4 | dnan线53-3 | dnan线53-4 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 266 | dnan线53-6~dnan线53-7 | dnan线53-6 | dnan线53-7 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 267 | dnan线53-4~dnan线53-5 | dnan线53-4 | dnan线53-5 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dnan | 墩南线 | PZXL-00092 | 墩集变 | 268 | 波士达支线4杆~波士达支线5杆 | 波士达支线4杆 | 波士达支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kVdnan线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 2 | dzhen线北支线10杆~dzhen线北支线11杆 | dzhen线北支线10杆 | dzhen线北支线11杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 3 | 王场湖支线1杆~王场湖支线2杆 | 王场湖支线1杆 | 王场湖支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 4 | 王场湖支线18杆~王场湖支线19杆 | 王场湖支线18杆 | 王场湖支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 5 | 王场湖支线21杆~王场湖支线22杆 | 王场湖支线21杆 | 王场湖支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 6 | 王场湖支线19杆~王场湖支线20杆 | 王场湖支线19杆 | 王场湖支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 7 | 王场湖支线17杆~王场湖支线18杆 | 王场湖支线17杆 | 王场湖支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 8 | 王场湖支线20杆~王场湖支线21杆 | 王场湖支线20杆 | 王场湖支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 9 | 王场湖支线14杆~王场湖支线15杆 | 王场湖支线14杆 | 王场湖支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 10 | 海天石化支线4杆~海天石化支线5杆 | 海天石化支线4杆 | 海天石化支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 11 | 海天石化支线16杆~海天石化支线17杆 | 海天石化支线16杆 | 海天石化支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 12 | 王场湖支线16杆~王场湖支线17杆 | 王场湖支线16杆 | 王场湖支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 13 | 海天石化支线9杆~海天石化支线10杆 | 海天石化支线9杆 | 海天石化支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 14 | 利峰支线2~利峰支线3 | 利峰支线2 | 利峰支线3 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 15 | dzhen线污水厂支线8杆~dzhen线污水厂支线9杆 | dzhen线污水厂支线8杆 | dzhen线污水厂支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 16 | dzhen线污水厂支线2杆~dzhen线污水厂支线3杆 | dzhen线污水厂支线2杆 | dzhen线污水厂支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 17 | 海天石化支线17杆~海天石化支线18杆 | 海天石化支线17杆 | 海天石化支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 18 | dzhen线正康支线4杆~dzhen线正康支线5杆 | dzhen线正康支线4杆 | dzhen线正康支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 19 | dzhen线污水厂支线20杆~dzhen线污水厂支线21杆 | dzhen线污水厂支线20杆 | dzhen线污水厂支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 20 | dzhen线昊阳支线3杆~dzhen线昊阳支线4杆 | dzhen线昊阳支线3杆 | dzhen线昊阳支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 21 | dzhen线污水厂支线13-1杆~dzhen线污水厂支线14杆 | dzhen线污水厂支线13-1杆 | dzhen线污水厂支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 22 | dzhen线污水厂支线15杆~dzhen线污水厂支线16杆 | dzhen线污水厂支线15杆 | dzhen线污水厂支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 23 | dzhen线南方永磁支线3杆~dzhen线南方永磁支线4杆 | dzhen线南方永磁支线3杆 | dzhen线南方永磁支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 24 | 海天石化支线19杆~dzhen线长运支线01杆 | 海天石化支线19杆 | dzhen线长运支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 25 | 王场湖支线13杆~王场湖支线14杆 | 王场湖支线13杆 | 王场湖支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 26 | 王场湖支线5杆~王场湖支线6杆 | 王场湖支线5杆 | 王场湖支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 27 | 海天石化支线13杆~海天石化支线14杆 | 海天石化支线13杆 | 海天石化支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 28 | dzhen线污水厂支线3杆~dzhen线污水厂支线4杆 | dzhen线污水厂支线3杆 | dzhen线污水厂支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 29 | dzhen线污水厂支线9杆~dzhen线污水厂支线10杆 | dzhen线污水厂支线9杆 | dzhen线污水厂支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 30 | 王场湖支线3杆~王场湖支线4杆 | 王场湖支线3杆 | 王场湖支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 31 | dzhen线污水厂支线16杆~dzhen线污水厂支线17杆 | dzhen线污水厂支线16杆 | dzhen线污水厂支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 32 | 利峰支线3~利峰支线4 | 利峰支线3 | 利峰支线4 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 33 | dzhen线污水厂支线17杆~dzhen线污水厂支线18杆 | dzhen线污水厂支线17杆 | dzhen线污水厂支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 34 | dzhen线污水厂支线13杆~王场湖支线1杆 | dzhen线污水厂支线13杆 | 王场湖支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 35 | dzhen线污水厂支线13杆~dzhen线污水厂支线13-1杆 | dzhen线污水厂支线13杆 | dzhen线污水厂支线13-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 36 | 王场湖支线15杆~王场湖支线16杆 | 王场湖支线15杆 | 王场湖支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 37 | dzhen线污水厂支线7杆~dzhen线昊阳支线1杆 | dzhen线污水厂支线7杆 | dzhen线昊阳支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 38 | dzhen线昊阳支线2杆~dzhen线昊阳支线3杆 | dzhen线昊阳支线2杆 | dzhen线昊阳支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 39 | 海天石化支线14杆~海天石化支线15杆 | 海天石化支线14杆 | 海天石化支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 40 | dzhen线昊阳支线1杆~dzhen线昊阳支线2杆 | dzhen线昊阳支线1杆 | dzhen线昊阳支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 41 | dzhen线污水厂支线21杆~dzhen线污水厂支线22杆 | dzhen线污水厂支线21杆 | dzhen线污水厂支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 42 | dzhen线污水厂支线22杆~dzhen线污水厂支线23杆 | dzhen线污水厂支线22杆 | dzhen线污水厂支线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 43 | 海天石化支线7杆~海天石化支线8杆 | 海天石化支线7杆 | 海天石化支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 44 | dzhen线15杆~dzhen线16杆 | dzhen线15杆 | dzhen线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 45 | dzhen线24杆~dzhen线25杆 | dzhen线24杆 | dzhen线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 46 | dzhen线01杆~dzhen线02杆 | dzhen线01杆 | dzhen线02杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 47 | dzhen线06杆~dzhen线北支线01杆 | dzhen线06杆 | dzhen线北支线01杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 48 | dzhen线恒鼎支线14杆~dzhen线恒鼎支线15杆 | dzhen线恒鼎支线14杆 | dzhen线恒鼎支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 49 | dzhen线15杆~利峰支线1 | dzhen线15杆 | 利峰支线1 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 50 | 王场湖支线9杆~王场湖支线10杆 | 王场湖支线9杆 | 王场湖支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 51 | 王场湖支线2杆~王场湖支线3杆 | 王场湖支线2杆 | 王场湖支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 52 | 王场湖支线8杆~王场湖支线9杆 | 王场湖支线8杆 | 王场湖支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 53 | 王场湖支线11杆~王场湖支线12杆 | 王场湖支线11杆 | 王场湖支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 54 | 海天石化支线12杆~海天石化支线13杆 | 海天石化支线12杆 | 海天石化支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 55 | dzhen线污水厂支线11杆~dzhen线污水厂支线12杆 | dzhen线污水厂支线11杆 | dzhen线污水厂支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 56 | dzhen线污水厂支线19杆~dzhen线污水厂支线20杆 | dzhen线污水厂支线19杆 | dzhen线污水厂支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 57 | dzhen线污水厂支线7杆~dzhen线污水厂支线8杆 | dzhen线污水厂支线7杆 | dzhen线污水厂支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 58 | 王场湖支线4杆~王场湖支线5杆 | 王场湖支线4杆 | 王场湖支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 59 | 王场湖支线10杆~王场湖支线11杆 | 王场湖支线10杆 | 王场湖支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 60 | dzhen线污水厂支线6杆~dzhen线污水厂支线7杆 | dzhen线污水厂支线6杆 | dzhen线污水厂支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 61 | 海天石化支线19杆~海天石化支线20杆 | 海天石化支线19杆 | 海天石化支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 62 | 海天石化支线3杆~海天石化支线4杆 | 海天石化支线3杆 | 海天石化支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 63 | dzhen线正康支线1杆~dzhen线正康支线2杆 | dzhen线正康支线1杆 | dzhen线正康支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 64 | 海天石化支线1杆~海天石化支线2杆 | 海天石化支线1杆 | 海天石化支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 65 | 海天石化支线21杆~海天石化支线22杆 | 海天石化支线21杆 | 海天石化支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 66 | 三仪支线01杆~三仪支线02杆 | 三仪支线01杆 | 三仪支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 67 | dzhen线41杆~dzhen线42杆 | dzhen线41杆 | dzhen线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 68 | dzhen线44杆~dzhen线45杆 | dzhen线44杆 | dzhen线45杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 69 | 海天石化支线11杆~海天石化支线12杆 | 海天石化支线11杆 | 海天石化支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 70 | 王场湖支线12杆~王场湖支线13杆 | 王场湖支线12杆 | 王场湖支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 71 | 海天石化支线15杆~海天石化支线16杆 | 海天石化支线15杆 | 海天石化支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 72 | dzhen线42杆~dzhen线43杆 | dzhen线42杆 | dzhen线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 73 | 海天石化支线5杆~海天石化支线6杆 | 海天石化支线5杆 | 海天石化支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 74 | 海天石化支线10杆~海天石化支线11杆 | 海天石化支线10杆 | 海天石化支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 75 | dzhen线昊阳支线4杆~dzhen线昊阳支线5杆 | dzhen线昊阳支线4杆 | dzhen线昊阳支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 76 | 海天石化支线2杆~海天石化支线3杆 | 海天石化支线2杆 | 海天石化支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 77 | dzhen线污水厂支线4杆~dzhen线污水厂支线5杆 | dzhen线污水厂支线4杆 | dzhen线污水厂支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 78 | dzhen线污水厂支线10杆~dzhen线污水厂支线11杆 | dzhen线污水厂支线10杆 | dzhen线污水厂支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 79 | 王场湖支线6杆~王场湖支线7杆 | 王场湖支线6杆 | 王场湖支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 80 | 海天石化支线6杆~海天石化支线7杆 | 海天石化支线6杆 | 海天石化支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 81 | 海天石化支线8杆~海天石化支线9杆 | 海天石化支线8杆 | 海天石化支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 82 | dzhen线长运支线01杆~dzhen线长运支线02杆 | dzhen线长运支线01杆 | dzhen线长运支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 83 | dzhen线污水厂支线12杆~dzhen线污水厂支线13杆 | dzhen线污水厂支线12杆 | dzhen线污水厂支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 84 | dzhen线43杆~dzhen线44杆 | dzhen线43杆 | dzhen线44杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 85 | 海天石化支线18杆~海天石化支线19杆 | 海天石化支线18杆 | 海天石化支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 86 | dzhen线正康支线2杆~dzhen线正康支线3杆 | dzhen线正康支线2杆 | dzhen线正康支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 87 | 海天石化支线20杆~海天石化支线21杆 | 海天石化支线20杆 | 海天石化支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 88 | dzhen线污水厂支线5杆~dzhen线污水厂支线6杆 | dzhen线污水厂支线5杆 | dzhen线污水厂支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 89 | dzhen线南方永磁支线2杆~dzhen线南方永磁支线3杆 | dzhen线南方永磁支线2杆 | dzhen线南方永磁支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 90 | dzhen线污水厂支线18杆~dzhen线污水厂支线19杆 | dzhen线污水厂支线18杆 | dzhen线污水厂支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 91 | dzhen线污水厂支线1杆~dzhen线污水厂支线2杆 | dzhen线污水厂支线1杆 | dzhen线污水厂支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 92 | 王场湖支线7杆~王场湖支线8杆 | 王场湖支线7杆 | 王场湖支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 93 | 利峰支线1~利峰支线2 | 利峰支线1 | 利峰支线2 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 94 | dzhen线正康支线3杆~dzhen线正康支线4杆 | dzhen线正康支线3杆 | dzhen线正康支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 95 | dzhen线恒鼎支线12杆~dzhen线恒鼎支线13杆 | dzhen线恒鼎支线12杆 | dzhen线恒鼎支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 96 | dzhen线恒鼎支线15杆~dzhen线恒鼎支线16杆 | dzhen线恒鼎支线15杆 | dzhen线恒鼎支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 97 | dzhen线30杆~dzhen线31杆 | dzhen线30杆 | dzhen线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 98 | dzhen线33杆~dzhen线34杆 | dzhen线33杆 | dzhen线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 99 | dzhen线11杆~dzhen线12杆 | dzhen线11杆 | dzhen线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 100 | dzhen线恒鼎支线7杆~dzhen线恒鼎支线8杆 | dzhen线恒鼎支线7杆 | dzhen线恒鼎支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 101 | dzhen线北支线01杆~dzhen线北支线02杆 | dzhen线北支线01杆 | dzhen线北支线02杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 102 | dzhen线19杆~dzhen线20杆 | dzhen线19杆 | dzhen线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 103 | dzhen线35杆~dzhen线36杆 | dzhen线35杆 | dzhen线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 104 | dzhen线31杆~dzhen线32杆 | dzhen线31杆 | dzhen线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 105 | dzhen线20杆~dzhen线21杆 | dzhen线20杆 | dzhen线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 106 | dzhen线38杆~dzhen线39杆 | dzhen线38杆 | dzhen线39杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 107 | dzhen线36杆~dzhen线37杆 | dzhen线36杆 | dzhen线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 108 | dzhen线09杆~dzhen线10杆 | dzhen线09杆 | dzhen线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 109 | dzhen线恒鼎支线3杆~dzhen线恒鼎支线4杆 | dzhen线恒鼎支线3杆 | dzhen线恒鼎支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 110 | dzhen线恒鼎支线11杆~dzhen线恒鼎支线12杆 | dzhen线恒鼎支线11杆 | dzhen线恒鼎支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 111 | dzhen线37杆~dzhen线38杆 | dzhen线37杆 | dzhen线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 112 | dzhen线34杆~dzhen线35杆 | dzhen线34杆 | dzhen线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 113 | dzhen线04杆~dzhen线05杆 | dzhen线04杆 | dzhen线05杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 114 | dzhen线23杆~dzhen线24杆 | dzhen线23杆 | dzhen线24杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 115 | dzhen线08杆~dzhen线09杆 | dzhen线08杆 | dzhen线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 116 | dzhen线39杆~dzhen线40杆 | dzhen线39杆 | dzhen线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 117 | dzhen线北支线03杆~dzhen线北支线04杆 | dzhen线北支线03杆 | dzhen线北支线04杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 118 | dzhen线恒鼎支线6杆~dzhen线恒鼎支线7杆 | dzhen线恒鼎支线6杆 | dzhen线恒鼎支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 119 | dzhen线恒鼎支线5杆~dzhen线恒鼎支线6杆 | dzhen线恒鼎支线5杆 | dzhen线恒鼎支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 120 | dzhen线21杆~dzhen线22杆 | dzhen线21杆 | dzhen线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 121 | dzhen线29杆~dzhen线30杆 | dzhen线29杆 | dzhen线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 122 | dzhen线18杆~dzhen线19杆 | dzhen线18杆 | dzhen线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 123 | dzhen线05杆~dzhen线06杆 | dzhen线05杆 | dzhen线06杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 124 | dzhen线02杆~dzhen线03杆 | dzhen线02杆 | dzhen线03杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 125 | dzhen线北支线04杆~dzhen线北支线05杆 | dzhen线北支线04杆 | dzhen线北支线05杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 126 | dzhen线03杆~dzhen线04杆 | dzhen线03杆 | dzhen线04杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 127 | dzhen线26杆~dzhen线27杆 | dzhen线26杆 | dzhen线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 128 | dzhen线16杆~dzhen线17杆 | dzhen线16杆 | dzhen线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 129 | dzhen线14杆~dzhen线15杆 | dzhen线14杆 | dzhen线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 130 | dzhen线22杆~dzhen线23杆 | dzhen线22杆 | dzhen线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 131 | dzhen线恒鼎支线2杆~dzhen线恒鼎支线3杆 | dzhen线恒鼎支线2杆 | dzhen线恒鼎支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 132 | dzhen线17杆~dzhen线18杆 | dzhen线17杆 | dzhen线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 133 | dzhen线恒鼎支线16杆~dzhen线恒鼎支线17杆 | dzhen线恒鼎支线16杆 | dzhen线恒鼎支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 134 | dzhen线10杆~dzhen线11杆 | dzhen线10杆 | dzhen线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 135 | dzhen线恒鼎支线4杆~dzhen线恒鼎支线5杆 | dzhen线恒鼎支线4杆 | dzhen线恒鼎支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 136 | dzhen线恒鼎支线9杆~dzhen线恒鼎支线10杆 | dzhen线恒鼎支线9杆 | dzhen线恒鼎支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 137 | dzhen线恒鼎支线10杆~dzhen线恒鼎支线11杆 | dzhen线恒鼎支线10杆 | dzhen线恒鼎支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 138 | dzhen线32杆~dzhen线33杆 | dzhen线32杆 | dzhen线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 139 | dzhen线25杆~dzhen线26杆 | dzhen线25杆 | dzhen线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 140 | dzhen线28杆~dzhen线29杆 | dzhen线28杆 | dzhen线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 141 | dzhen线恒鼎支线8杆~dzhen线恒鼎支线9杆 | dzhen线恒鼎支线8杆 | dzhen线恒鼎支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 142 | dzhen线恒鼎支线13杆~dzhen线恒鼎支线14杆 | dzhen线恒鼎支线13杆 | dzhen线恒鼎支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 143 | dzhen线12杆~dzhen线13杆 | dzhen线12杆 | dzhen线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 144 | dzhen线北支线02杆~dzhen线北支线03杆 | dzhen线北支线02杆 | dzhen线北支线03杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 145 | dzhen线27杆~dzhen线28杆 | dzhen线27杆 | dzhen线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 146 | dzhen线40杆~dzhen线41杆 | dzhen线40杆 | dzhen线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 147 | dzhen线13杆~dzhen线14杆 | dzhen线13杆 | dzhen线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 148 | dzhen线力达支线3杆~dzhen线力达支线4杆 | dzhen线力达支线3杆 | dzhen线力达支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 149 | dzhen线污水厂支线4杆~dzhen线力达支线1杆 | dzhen线污水厂支线4杆 | dzhen线力达支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 150 | dzhen线力达支线1杆~dzhen线力达支线2杆 | dzhen线力达支线1杆 | dzhen线力达支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 151 | dzhen线力达支线2杆~dzhen线力达支线3杆 | dzhen线力达支线2杆 | dzhen线力达支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 152 | dzhen线恒鼎支线10杆~dzhen线正康支线1杆 | dzhen线恒鼎支线10杆 | dzhen线正康支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 153 | dzhen线33杆~三仪支线01杆 | dzhen线33杆 | 三仪支线01杆 | 50 | JKLYJ-240/10 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 154 | dzhen线15杆~海天石化支线1杆 | dzhen线15杆 | 海天石化支线1杆 | 50 | JKLYJ-240/10 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 155 | dzhen线06杆~dzhen线07杆 | dzhen线06杆 | dzhen线07杆 | 50 | JKLGYJ-70 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 156 | dzhen线污水厂支线14杆~dzhen线污水厂支线15杆 | dzhen线污水厂支线14杆 | dzhen线污水厂支线15杆 | 50 | JKLYJ-240/10 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 157 | dzhen线正康支线8杆~dzhen线正康支线9杆 | dzhen线正康支线8杆 | dzhen线正康支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 158 | dzhen线正康支线6杆~dzhen线正康支线7杆 | dzhen线正康支线6杆 | dzhen线正康支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 159 | dzhen线正康支线9杆~dzhen线正康支线10杆 | dzhen线正康支线9杆 | dzhen线正康支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 160 | dzhen线正康支线7杆~dzhen线正康支线8杆 | dzhen线正康支线7杆 | dzhen线正康支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 161 | dzhen线正康支线5杆~dzhen线正康支线6杆 | dzhen线正康支线5杆 | dzhen线正康支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩振线明细.xlsx
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 162 | dzhen线29杆~dzhen线29-1 | dzhen线29杆 | dzhen线29-1 | 50 | JLRX/T-120/30 | 邳州_10kV墩振线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 2 | dxi线王场湖支线7-4~dxi线王场湖支线7-5 | dxi线王场湖支线7-4 | dxi线王场湖支线7-5 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 3 | dxi线王场湖支线7-2~dxi线王场湖支线7-3 | dxi线王场湖支线7-2 | dxi线王场湖支线7-3 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 4 | dxi线王场湖支线07~dxi线王场湖支线7-1 | dxi线王场湖支线07 | dxi线王场湖支线7-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 5 | dxi线王场湖支线7-3~dxi线王场湖支线7-4 | dxi线王场湖支线7-3 | dxi线王场湖支线7-4 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 6 | dxi线王场湖支线7-1~dxi线王场湖支线7-2 | dxi线王场湖支线7-1 | dxi线王场湖支线7-2 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 7 | dxi线44杆~dxi线44-1杆 | dxi线44杆 | dxi线44-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 8 | dxi线06杆~dxi线07杆 | dxi线06杆 | dxi线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 9 | dxi线王场湖支线09~dxi线高速路变支线01杆 | dxi线王场湖支线09 | dxi线高速路变支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 10 | dxi线海天石化支线31~dxi线兴春支线01杆 | dxi线海天石化支线31 | dxi线兴春支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 11 | dxi线海天石化支线41杆~dxi线海天石化支线42杆 | dxi线海天石化支线41杆 | dxi线海天石化支线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 12 | dxi线兴春支线02杆~dxi线兴春支线03杆 | dxi线兴春支线02杆 | dxi线兴春支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 13 | dxi线海天石化支线43杆~dxi线海天石化支线44杆 | dxi线海天石化支线43杆 | dxi线海天石化支线44杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 14 | dxi线海天石化支线40杆~dxi线海天石化支线41杆 | dxi线海天石化支线40杆 | dxi线海天石化支线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 15 | dxi线兴春支线03杆~dxi线兴春支线04杆 | dxi线兴春支线03杆 | dxi线兴春支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 16 | dxi线06杆~dxi北支线1杆 | dxi线06杆 | dxi北支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 17 | dxi线海天石化支线42杆~dxi线海天石化支线43杆 | dxi线海天石化支线42杆 | dxi线海天石化支线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 18 | dxi线兴春支线01杆~dxi线兴春支线02杆 | dxi线兴春支线01杆 | dxi线兴春支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 19 | dxi线海天石化支线37~dxi线王场湖支线01 | dxi线海天石化支线37 | dxi线王场湖支线01 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 20 | dxi线09杆~dxi线10杆 | dxi线09杆 | dxi线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 21 | dxi线14杆~dxi线15杆 | dxi线14杆 | dxi线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 22 | dxi线08杆~dxi线09杆 | dxi线08杆 | dxi线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 23 | dxi线13杆~dxi线14杆 | dxi线13杆 | dxi线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 24 | dxi北支线9杆~dxi北支线10杆 | dxi北支线9杆 | dxi北支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 25 | dxi线20杆~dxi线21杆 | dxi线20杆 | dxi线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 26 | dxi线12杆~dxi线13杆 | dxi线12杆 | dxi线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 27 | dxi北支线8杆~dxi北支线9杆 | dxi北支线8杆 | dxi北支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 28 | dxi北支线3杆~dxi北支线4杆 | dxi北支线3杆 | dxi北支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 29 | dxi线16杆~dxi线17杆 | dxi线16杆 | dxi线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 30 | dxi线10杆~dxi线11杆 | dxi线10杆 | dxi线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 31 | dxi线03杆~dxi线04杆 | dxi线03杆 | dxi线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 32 | dxi线11杆~dxi线12杆 | dxi线11杆 | dxi线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 33 | dxi线海天石化支线11~dxi线海天石化支线12 | dxi线海天石化支线11 | dxi线海天石化支线12 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 34 | dxi线海天石化支线14~dxi线海天石化支线15 | dxi线海天石化支线14 | dxi线海天石化支线15 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 35 | dxi线王场湖支线01~dxi线王场湖支线02 | dxi线王场湖支线01 | dxi线王场湖支线02 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 36 | dxi线王场湖支线03~dxi线王场湖支线04 | dxi线王场湖支线03 | dxi线王场湖支线04 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 37 | dxi线王场湖支线06~dxi线王场湖支线07 | dxi线王场湖支线06 | dxi线王场湖支线07 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 38 | dxi线王场湖支线12~dxi线王场湖支线13 | dxi线王场湖支线12 | dxi线王场湖支线13 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 39 | dxi线王场湖支线11~dxi线王场湖支线12 | dxi线王场湖支线11 | dxi线王场湖支线12 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 40 | dxi线海天石化支线31~dxi线海天石化支线32 | dxi线海天石化支线31 | dxi线海天石化支线32 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 41 | dxi线海天石化支线37~dxi线海天石化支线38 | dxi线海天石化支线37 | dxi线海天石化支线38 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 42 | dxi线海天石化支线05~dxi线海天石化支线06 | dxi线海天石化支线05 | dxi线海天石化支线06 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 43 | dxi线海天石化支线16~dxi线海天石化支线17 | dxi线海天石化支线16 | dxi线海天石化支线17 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 44 | dxi线海天石化支线36~dxi线海天石化支线37 | dxi线海天石化支线36 | dxi线海天石化支线37 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 45 | dxi线海天石化支线39~dxi线海天石化支线40杆 | dxi线海天石化支线39 | dxi线海天石化支线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 46 | dxi线26杆~dxi线27杆 | dxi线26杆 | dxi线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 47 | dxi北支线11杆~dxi北支线12杆 | dxi北支线11杆 | dxi北支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 48 | dxi北支线14杆~dxi北支线15杆 | dxi北支线14杆 | dxi北支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 49 | dxi北支线24杆~dxi北支线25杆 | dxi北支线24杆 | dxi北支线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 50 | dxi线34杆~dxi线35杆 | dxi线34杆 | dxi线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 51 | dxi北支线29杆~dxi北支线30杆 | dxi北支线29杆 | dxi北支线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 52 | dxi北支线19杆~dxi北支线20杆 | dxi北支线19杆 | dxi北支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 53 | dxi线海天石化支线01~dxi线海天石化支线02 | dxi线海天石化支线01 | dxi线海天石化支线02 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 54 | dxi线31杆~dxi线32杆 | dxi线31杆 | dxi线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 55 | dxi线38杆~dxi线39杆 | dxi线38杆 | dxi线39杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 56 | dxi北支线34杆~dxi北支线35杆 | dxi北支线34杆 | dxi北支线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 57 | dxi北支线36杆~dxi北支线37杆 | dxi北支线36杆 | dxi北支线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 58 | dxi北支线28杆~dxi北支线29杆 | dxi北支线28杆 | dxi北支线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 59 | dxi北支线33杆~dxi北支线34杆 | dxi北支线33杆 | dxi北支线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 60 | dxi北支线38杆~dxi北支线39杆 | dxi北支线38杆 | dxi北支线39杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 61 | dxi线海天石化支线34~dxi线海天石化支线35 | dxi线海天石化支线34 | dxi线海天石化支线35 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 62 | dxi线王场湖支线09~dxi线王场湖支线10 | dxi线王场湖支线09 | dxi线王场湖支线10 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 63 | dxi线海天石化支线10~dxi线海天石化支线11 | dxi线海天石化支线10 | dxi线海天石化支线11 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 64 | dxi线王场湖支线13~dxi线王场湖支线14 | dxi线王场湖支线13 | dxi线王场湖支线14 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 65 | dxi线海天石化支线20~dxi线海天石化支线21 | dxi线海天石化支线20 | dxi线海天石化支线21 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 66 | dxi线海天石化支线28~dxi线海天石化支线29 | dxi线海天石化支线28 | dxi线海天石化支线29 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 67 | dxi北支线31杆~dxi北支线32杆 | dxi北支线31杆 | dxi北支线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 68 | dxi线海天石化支线32~dxi线海天石化支线33 | dxi线海天石化支线32 | dxi线海天石化支线33 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 69 | dxi线海天石化支线33~dxi线海天石化支线34 | dxi线海天石化支线33 | dxi线海天石化支线34 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 70 | dxi北支线16杆~dxi北支线17杆 | dxi北支线16杆 | dxi北支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 71 | dxi线30杆~dxi线31杆 | dxi线30杆 | dxi线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 72 | dxi线32杆~dxi线33杆 | dxi线32杆 | dxi线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 73 | dxi线王场湖支线10~dxi线王场湖支线11 | dxi线王场湖支线10 | dxi线王场湖支线11 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 74 | dxi线王场湖支线04~dxi线王场湖支线05 | dxi线王场湖支线04 | dxi线王场湖支线05 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 75 | dxi线海天石化支线24~dxi线海天石化支线25 | dxi线海天石化支线24 | dxi线海天石化支线25 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 76 | dxi线海天石化支线08~dxi线海天石化支线09 | dxi线海天石化支线08 | dxi线海天石化支线09 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 77 | dxi线海天石化支线12~dxi线海天石化支线13 | dxi线海天石化支线12 | dxi线海天石化支线13 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 78 | dxi线海天石化支线17~dxi线海天石化支线18 | dxi线海天石化支线17 | dxi线海天石化支线18 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 79 | dxi北支线17杆~dxi北支线18杆 | dxi北支线17杆 | dxi北支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 80 | dxi北支线25杆~dxi北支线26杆 | dxi北支线25杆 | dxi北支线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 81 | dxi线29杆~dxi线30杆 | dxi线29杆 | dxi线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 82 | dxi线39杆~dxi线40杆 | dxi线39杆 | dxi线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 83 | dxi北支线26杆~dxi北支线27杆 | dxi北支线26杆 | dxi北支线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 84 | dxi线15杆~dxi线海天石化支线01 | dxi线15杆 | dxi线海天石化支线01 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 85 | dxi线海天石化支线03~dxi线海天石化支线04 | dxi线海天石化支线03 | dxi线海天石化支线04 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 86 | dxi北支线42杆~dxi北支线43杆 | dxi北支线42杆 | dxi北支线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 87 | dxi北支线22杆~dxi北支线23杆 | dxi北支线22杆 | dxi北支线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 88 | dxi北支线23杆~dxi北支线24杆 | dxi北支线23杆 | dxi北支线24杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 89 | dxi线王场湖支线07~dxi线王场湖支线08 | dxi线王场湖支线07 | dxi线王场湖支线08 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 90 | dxi线35杆~dxi线36杆 | dxi线35杆 | dxi线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 91 | dxi线37杆~dxi线38杆 | dxi线37杆 | dxi线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 92 | dxi北支线30杆~dxi北支线31杆 | dxi北支线30杆 | dxi北支线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 93 | dxi线海天石化支线38~dxi线海天石化支线39 | dxi线海天石化支线38 | dxi线海天石化支线39 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 94 | dxi线海天石化支线02~dxi线海天石化支线03 | dxi线海天石化支线02 | dxi线海天石化支线03 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 95 | dxi线海天石化支线07~dxi线海天石化支线08 | dxi线海天石化支线07 | dxi线海天石化支线08 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 96 | dxi线海天石化支线27~dxi线海天石化支线28 | dxi线海天石化支线27 | dxi线海天石化支线28 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 97 | dxi线海天石化支线29~dxi线海天石化支线30 | dxi线海天石化支线29 | dxi线海天石化支线30 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 98 | dxi北支线21杆~dxi北支线22杆 | dxi北支线21杆 | dxi北支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 99 | dxi线海天石化支线04~dxi线海天石化支线05 | dxi线海天石化支线04 | dxi线海天石化支线05 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 100 | dxi线海天石化支线26~dxi线海天石化支线27 | dxi线海天石化支线26 | dxi线海天石化支线27 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 101 | dxi线41杆~dxi线42杆 | dxi线41杆 | dxi线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 102 | dxi北支线5杆~dxi北支线6杆 | dxi北支线5杆 | dxi北支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 103 | dxi线01杆~dxi线02杆 | dxi线01杆 | dxi线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 104 | dxi线王场湖支线02~dxi线王场湖支线03 | dxi线王场湖支线02 | dxi线王场湖支线03 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 105 | dxi线海天石化支线09~dxi线海天石化支线10 | dxi线海天石化支线09 | dxi线海天石化支线10 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 106 | dxi线海天石化支线13~dxi线海天石化支线14 | dxi线海天石化支线13 | dxi线海天石化支线14 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 107 | dxi线海天石化支线19~dxi线海天石化支线20 | dxi线海天石化支线19 | dxi线海天石化支线20 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 108 | dxi线海天石化支线35~dxi线海天石化支线36 | dxi线海天石化支线35 | dxi线海天石化支线36 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 109 | dxi线海天石化支线23~dxi线海天石化支线24 | dxi线海天石化支线23 | dxi线海天石化支线24 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 110 | dxi北支线18杆~dxi北支线19杆 | dxi北支线18杆 | dxi北支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 111 | dxi北支线32杆~dxi北支线33杆 | dxi北支线32杆 | dxi北支线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 112 | dxi线33杆~dxi线34杆 | dxi线33杆 | dxi线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 113 | dxi线36杆~dxi线37杆 | dxi线36杆 | dxi线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 114 | dxi北支线20杆~dxi北支线21杆 | dxi北支线20杆 | dxi北支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 115 | dxi北支线27杆~dxi北支线28杆 | dxi北支线27杆 | dxi北支线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 116 | dxi北支线35杆~dxi北支线36杆 | dxi北支线35杆 | dxi北支线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 117 | dxi线27杆~dxi线28杆 | dxi线27杆 | dxi线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 118 | dxi北支线12杆~dxi北支线13杆 | dxi北支线12杆 | dxi北支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 119 | dxi北支线37杆~dxi北支线38杆 | dxi北支线37杆 | dxi北支线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 120 | dxi线40杆~dxi线41杆 | dxi线40杆 | dxi线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 121 | dxi北支线13杆~dxi北支线14杆 | dxi北支线13杆 | dxi北支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 122 | dxi线王场湖支线08~dxi线王场湖支线09 | dxi线王场湖支线08 | dxi线王场湖支线09 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 123 | dxi线海天石化支线18~dxi线海天石化支线19 | dxi线海天石化支线18 | dxi线海天石化支线19 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 124 | dxi线海天石化支线25~dxi线海天石化支线26 | dxi线海天石化支线25 | dxi线海天石化支线26 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 125 | dxi线海天石化支线21~dxi线海天石化支线22 | dxi线海天石化支线21 | dxi线海天石化支线22 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 126 | dxi线海天石化支线22~dxi线海天石化支线23 | dxi线海天石化支线22 | dxi线海天石化支线23 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 127 | dxi线海天石化支线15~dxi线海天石化支线16 | dxi线海天石化支线15 | dxi线海天石化支线16 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 128 | dxi线海天石化支线30~dxi线海天石化支线31 | dxi线海天石化支线30 | dxi线海天石化支线31 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 129 | dxi线25杆~dxi线26杆 | dxi线25杆 | dxi线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 130 | dxi北支线39杆~dxi北支线40杆 | dxi北支线39杆 | dxi北支线40杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 131 | dxi北支线40杆~dxi北支线41杆 | dxi北支线40杆 | dxi北支线41杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 132 | dxi线28杆~dxi线29杆 | dxi线28杆 | dxi线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 133 | dxi线海天石化支线06~dxi线海天石化支线07 | dxi线海天石化支线06 | dxi线海天石化支线07 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 134 | dxi北支线15杆~dxi北支线16杆 | dxi北支线15杆 | dxi北支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 135 | dxi线王场湖支线05~dxi线王场湖支线06 | dxi线王场湖支线05 | dxi线王场湖支线06 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 136 | dxi北支线41杆~dxi北支线42杆 | dxi北支线41杆 | dxi北支线42杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 137 | dxi线15杆~dxi线16杆 | dxi线15杆 | dxi线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 138 | dxi线24杆~dxi线25杆 | dxi线24杆 | dxi线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 139 | dxi线合金厂支线01杆~dxi线合金厂支线02杆 | dxi线合金厂支线01杆 | dxi线合金厂支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 140 | dxi线企服中心支线5杆~dxi线企服中心支线6杆 | dxi线企服中心支线5杆 | dxi线企服中心支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 141 | dxi线企服中心支线14杆~dxi线企服中心支线15杆 | dxi线企服中心支线14杆 | dxi线企服中心支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 142 | dxi线企服中心支线4杆~dxi线企服中心支线5杆 | dxi线企服中心支线4杆 | dxi线企服中心支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 143 | dxi线24杆~dxi线企服中心支线1杆 | dxi线24杆 | dxi线企服中心支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 144 | dxi线企服中心支线11杆~dxi线企服中心支线12杆 | dxi线企服中心支线11杆 | dxi线企服中心支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 145 | dxi线企服中心支线10杆~dxi线企服中心支线11杆 | dxi线企服中心支线10杆 | dxi线企服中心支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 146 | dxi线企服中心支线1杆~dxi线企服中心支线2杆 | dxi线企服中心支线1杆 | dxi线企服中心支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 147 | dxi线企服中心支线8杆~dxi线企服中心支线9杆 | dxi线企服中心支线8杆 | dxi线企服中心支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 148 | dxi线企服中心支线12杆~dxi线企服中心支线13杆 | dxi线企服中心支线12杆 | dxi线企服中心支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 149 | dxi线企服中心支线15杆~dxi线企服中心支线16杆 | dxi线企服中心支线15杆 | dxi线企服中心支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 150 | dxi线企服中心支线2杆~dxi线企服中心支线3杆 | dxi线企服中心支线2杆 | dxi线企服中心支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 151 | dxi线企服中心支线6杆~dxi线企服中心支线7杆 | dxi线企服中心支线6杆 | dxi线企服中心支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 152 | dxi线企服中心支线7杆~dxi线企服中心支线8杆 | dxi线企服中心支线7杆 | dxi线企服中心支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 153 | dxi线企服中心支线3杆~dxi线企服中心支线4杆 | dxi线企服中心支线3杆 | dxi线企服中心支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 154 | dxi线企服中心支线9杆~dxi线企服中心支线10杆 | dxi线企服中心支线9杆 | dxi线企服中心支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 155 | dxi线企服中心支线16杆~dxi线企服中心支线17杆 | dxi线企服中心支线16杆 | dxi线企服中心支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 156 | dxi线企服中心支线13杆~dxi线企服中心支线14杆 | dxi线企服中心支线13杆 | dxi线企服中心支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 157 | dxi北支线10杆~dxi北支线11杆 | dxi北支线10杆 | dxi北支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 158 | dxi线海天石化支线15~dxi线合金厂支线01杆 | dxi线海天石化支线15 | dxi线合金厂支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 159 | dxi线02杆~dxi线03杆 | dxi线02杆 | dxi线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 160 | dxi北支线1杆~dxi北支线2杆 | dxi北支线1杆 | dxi北支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 161 | dxi线42杆~dxi线43杆 | dxi线42杆 | dxi线43杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 162 | dxi北支线7杆~dxi北支线8杆 | dxi北支线7杆 | dxi北支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 163 | dxi北支线4杆~dxi北支线5杆 | dxi北支线4杆 | dxi北支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 164 | dxi线05杆~dxi线06杆 | dxi线05杆 | dxi线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 165 | dxi线07杆~dxi线08杆 | dxi线07杆 | dxi线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 166 | dxi线21杆~dxi线22杆 | dxi线21杆 | dxi线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 167 | dxi线19杆~dxi线20杆 | dxi线19杆 | dxi线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 168 | dxi线43杆~dxi线44杆 | dxi线43杆 | dxi线44杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 169 | dxi北支线6杆~dxi北支线7杆 | dxi北支线6杆 | dxi北支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 170 | dxi线04杆~dxi线05杆 | dxi线04杆 | dxi线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 171 | dxi线22杆~dxi线23杆 | dxi线22杆 | dxi线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 172 | dxi北支线2杆~dxi北支线3杆 | dxi北支线2杆 | dxi北支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 173 | dxi线18杆~dxi线19杆 | dxi线18杆 | dxi线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 174 | dxi线17杆~dxi线18杆 | dxi线17杆 | dxi线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 175 | dxi线13杆~dxi线13-1杆 | dxi线13杆 | dxi线13-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 176 | dxi北支线38杆~dxi线北支线38-1杆 | dxi北支线38杆 | dxi线北支线38-1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 177 | dxi线国成支线4杆~dxi线国成支线5杆 | dxi线国成支线4杆 | dxi线国成支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 178 | dxi线国成支线3杆~dxi线国成支线4杆 | dxi线国成支线3杆 | dxi线国成支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 179 | dxi线国成支线7杆~dxi线国成支线8杆 | dxi线国成支线7杆 | dxi线国成支线8杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 180 | dxi线国成支线6杆~dxi线国成支线7杆 | dxi线国成支线6杆 | dxi线国成支线7杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 181 | dxi线国成支线8杆~dxi线国成支线9杆 | dxi线国成支线8杆 | dxi线国成支线9杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 182 | dxi线国成支线5杆~dxi线国成支线6杆 | dxi线国成支线5杆 | dxi线国成支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 183 | dxi线国成支线9杆~dxi线国成支线10杆 | dxi线国成支线9杆 | dxi线国成支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 184 | dxi线国成支线2杆~dxi线国成支线3杆 | dxi线国成支线2杆 | dxi线国成支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 185 | dxi线国成支线1杆~dxi线国成支线2杆 | dxi线国成支线1杆 | dxi线国成支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 186 | dxi线海天石化支线15~dxi线国成支线1杆 | dxi线海天石化支线15 | dxi线国成支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 187 | dxi线日托支线4杆~dxi线日托支线5杆 | dxi线日托支线4杆 | dxi线日托支线5杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 188 | dxi线44杆~dxi线日托支线1杆 | dxi线44杆 | dxi线日托支线1杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 189 | dxi线日托支线3杆~dxi线日托支线4杆 | dxi线日托支线3杆 | dxi线日托支线4杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 190 | dxi线日托支线2杆~dxi线日托支线3杆 | dxi线日托支线2杆 | dxi线日托支线3杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 191 | dxi线日托支线5杆~dxi线日托支线6杆 | dxi线日托支线5杆 | dxi线日托支线6杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
dxi | 墩西线 | PZXL-00097 | 墩集变 | 192 | dxi线日托支线1杆~dxi线日托支线2杆 | dxi线日托支线1杆 | dxi线日托支线2杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV墩西线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 2 | hdong线44杆~河湾1#支线01杆 | hdong线44杆 | 河湾1#支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 3 | hdong线56杆~hdong线56-1杆 | hdong线56杆 | hdong线56-1杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 4 | hdong线61杆~hdong线62杆 | hdong线61杆 | hdong线62杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 5 | hdong线79-2杆~hdong线79-3杆 | hdong线79-2杆 | hdong线79-3杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 6 | 煤球厂支线02杆~煤球厂支线03杆 | 煤球厂支线02杆 | 煤球厂支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 7 | hdong线14杆~hdong线15杆 | hdong线14杆 | hdong线15杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 8 | hdong线17杆~hdong线18杆 | hdong线17杆 | hdong线18杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 9 | 河湾1#支线11杆~河湾1#支线12杆 | 河湾1#支线11杆 | 河湾1#支线12杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 10 | 贝斯卡拉支线001杆~贝斯卡拉支线002杆 | 贝斯卡拉支线001杆 | 贝斯卡拉支线002杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 11 | hdong线22杆~hdong线23杆 | hdong线22杆 | hdong线23杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 12 | hdong线79-3杆~hdong线79-4杆 | hdong线79-3杆 | hdong线79-4杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 13 | 煤球厂支线03杆~煤球厂支线04杆 | 煤球厂支线03杆 | 煤球厂支线04杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 14 | 日松馆业支线02杆~日松馆业支线03杆 | 日松馆业支线02杆 | 日松馆业支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 15 | hdong线15杆~hdong线16杆 | hdong线15杆 | hdong线16杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 16 | hdong线21杆~hdong线22杆 | hdong线21杆 | hdong线22杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 17 | 河湾1#支线14杆~河湾1#支线15杆 | 河湾1#支线14杆 | 河湾1#支线15杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 18 | hdong线16杆~hdong线17杆 | hdong线16杆 | hdong线17杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 19 | hdong线80杆~hdong线79-1杆 | hdong线80杆 | hdong线79-1杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 20 | hdong线18杆~hdong线19杆 | hdong线18杆 | hdong线19杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 21 | 李口八队电站支线02~李口八队电站支线03 | 李口八队电站支线02 | 李口八队电站支线03 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 22 | 煤球厂支线01杆~煤球厂支线02杆 | 煤球厂支线01杆 | 煤球厂支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 23 | hdong线10杆~hdong线11杆 | hdong线10杆 | hdong线11杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 24 | hdong线37杆~hdong线38杆 | hdong线37杆 | hdong线38杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 25 | hdong线65杆~日松馆业支线01杆 | hdong线65杆 | 日松馆业支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 26 | hdong线40杆~hdong线41杆 | hdong线40杆 | hdong线41杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 27 | hdong线69杆~hdong支线01杆 | hdong线69杆 | hdong支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 28 | hdong线65杆~华运蒜业支线01杆 | hdong线65杆 | 华运蒜业支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 29 | hdong线43杆~hdong线44杆 | hdong线43杆 | hdong线44杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 30 | hdong线26杆~hdong线27杆 | hdong线26杆 | hdong线27杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 31 | hdong线27杆~hdong线28杆 | hdong线27杆 | hdong线28杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 32 | 河湾1#支线12杆~河湾1#支线13杆 | 河湾1#支线12杆 | 河湾1#支线13杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 33 | 河湾1#支线10杆~河湾1#支线11杆 | 河湾1#支线10杆 | 河湾1#支线11杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 34 | 河湾1#支线09杆~河湾1#支线10杆 | 河湾1#支线09杆 | 河湾1#支线10杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 35 | hdong线19杆~hdong线20杆 | hdong线19杆 | hdong线20杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 36 | hdong线13杆~hdong线14杆 | hdong线13杆 | hdong线14杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 37 | 李口八队电站支线01~李口八队电站支线02 | 李口八队电站支线01 | 李口八队电站支线02 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 38 | hdong线24杆~煤球厂支线01杆 | hdong线24杆 | 煤球厂支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 39 | hdong线张村2#变支线07杆~hdong线张村2#变支线07-1杆 | hdong线张村2#变支线07杆 | hdong线张村2#变支线07-1杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 40 | 日松馆业支线01杆~日松馆业支线02杆 | 日松馆业支线01杆 | 日松馆业支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 41 | 华运蒜业支线02杆~华运蒜业支线03杆 | 华运蒜业支线02杆 | 华运蒜业支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 42 | hdong线79-1杆~hdong线79-2杆 | hdong线79-1杆 | hdong线79-2杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 43 | hdong线79-1杆~贝斯卡拉支线001杆 | hdong线79-1杆 | 贝斯卡拉支线001杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 44 | hdong线74-04杆~hdong线74-05杆 | hdong线74-04杆 | hdong线74-05杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 45 | hdong线79-3杆~环境卫生管理处支线01杆 | hdong线79-3杆 | 环境卫生管理处支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 46 | hdong线张村2#变支线16杆~hdong线张村2#变支线17杆 | hdong线张村2#变支线16杆 | hdong线张村2#变支线17杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 47 | hdong线29杆~hdong线30杆 | hdong线29杆 | hdong线30杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 48 | hdong线张村2#变支线15杆~hdong线张村2#变支线16杆 | hdong线张村2#变支线15杆 | hdong线张村2#变支线16杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 49 | hdong线汇龙支线08杆~hdong线汇龙支线09杆 | hdong线汇龙支线08杆 | hdong线汇龙支线09杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 50 | hdong线1杆~hdong线2杆 | hdong线1杆 | hdong线2杆 | 50 | JLB3-35 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 51 | hdong线3杆~hdong线4杆 | hdong线3杆 | hdong线4杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 52 | hdong线4杆~hdong线5杆 | hdong线4杆 | hdong线5杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 53 | hdong线32杆~hdong线33杆 | hdong线32杆 | hdong线33杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 54 | hdong线31杆~hdong线32杆 | hdong线31杆 | hdong线32杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 55 | hdong线30杆~hdong线31杆 | hdong线30杆 | hdong线31杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 56 | hdong线张村2#变支线09杆~hdong线张村2#变支线10杆 | hdong线张村2#变支线09杆 | hdong线张村2#变支线10杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 57 | hdong线张村2#变支线02杆~hdong线张村2#变支线03杆 | hdong线张村2#变支线02杆 | hdong线张村2#变支线03杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 58 | hdong线5杆~hdong线6杆 | hdong线5杆 | hdong线6杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 59 | hdong线7杆~hdong线8杆 | hdong线7杆 | hdong线8杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 60 | hdong线2杆~hdong线3杆 | hdong线2杆 | hdong线3杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 61 | hdong线张村2#变支线18杆~hdong线张村2#变支线19杆 | hdong线张村2#变支线18杆 | hdong线张村2#变支线19杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 62 | hdong线汇龙支线03杆~hdong线汇龙支线04杆 | hdong线汇龙支线03杆 | hdong线汇龙支线04杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 63 | hdong线张村2#变支线05杆~hdong线张村2#变支线06杆 | hdong线张村2#变支线05杆 | hdong线张村2#变支线06杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 64 | hdong线张村2#变支线10杆~hdong线张村2#变支线11杆 | hdong线张村2#变支线10杆 | hdong线张村2#变支线11杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 65 | hdong线6杆~hdong线7杆 | hdong线6杆 | hdong线7杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 66 | hdong线张村2#变支线14杆~hdong线张村2#变支线15杆 | hdong线张村2#变支线14杆 | hdong线张村2#变支线15杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 67 | hdong线23杆~hdong线汇龙支线01杆 | hdong线23杆 | hdong线汇龙支线01杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 68 | hdong线28杆~hdong线29杆 | hdong线28杆 | hdong线29杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 69 | hdong线张村2#变支线04杆~hdong线张村2#变支线05杆 | hdong线张村2#变支线04杆 | hdong线张村2#变支线05杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 70 | hdong线张村2#变支线08杆~hdong线张村2#变支线09杆 | hdong线张村2#变支线08杆 | hdong线张村2#变支线09杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 71 | hdong线张村2#变支线12杆~hdong线张村2#变支线13杆 | hdong线张村2#变支线12杆 | hdong线张村2#变支线13杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 72 | hdong线汇龙支线02杆~hdong线汇龙支线03杆 | hdong线汇龙支线02杆 | hdong线汇龙支线03杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 73 | hdong线汇龙支线06杆~hdong线汇龙支线07杆 | hdong线汇龙支线06杆 | hdong线汇龙支线07杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 74 | hdong线汇龙支线10杆~hdong线汇龙支线11杆 | hdong线汇龙支线10杆 | hdong线汇龙支线11杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 75 | hdong线69杆~hdong线70杆 | hdong线69杆 | hdong线70杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 76 | hdong线70杆~hdong线71杆 | hdong线70杆 | hdong线71杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 77 | hdong线71杆~hdong线72杆 | hdong线71杆 | hdong线72杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 78 | hdong线65杆~hdong线66杆 | hdong线65杆 | hdong线66杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 79 | hdong线58杆~hdong线59杆 | hdong线58杆 | hdong线59杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 80 | hdong线57杆~hdong线58杆 | hdong线57杆 | hdong线58杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 81 | hdong线54杆~hdong线55杆 | hdong线54杆 | hdong线55杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 82 | hdong线55杆~hdong线56杆 | hdong线55杆 | hdong线56杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 83 | hdong线56杆~hdong线57杆 | hdong线56杆 | hdong线57杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 84 | hdong线53杆~hdong线54杆 | hdong线53杆 | hdong线54杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 85 | hdong线52杆~hdong线53杆 | hdong线52杆 | hdong线53杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 86 | hdong线62杆~hdong线63杆 | hdong线62杆 | hdong线63杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 87 | hdong线63杆~hdong线64杆 | hdong线63杆 | hdong线64杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 88 | hdong线64杆~hdong线65杆 | hdong线64杆 | hdong线65杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 89 | hdong线92杆~hdong线93杆 | hdong线92杆 | hdong线93杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 90 | hdong线81杆~hdong线82杆 | hdong线81杆 | hdong线82杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 91 | hdong线82杆~hdong线83杆 | hdong线82杆 | hdong线83杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 92 | hdong线83杆~hdong线84杆 | hdong线83杆 | hdong线84杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 93 | hdong线84杆~hdong线85杆 | hdong线84杆 | hdong线85杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 94 | hdong线85杆~hdong线86杆 | hdong线85杆 | hdong线86杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 95 | hdong线86杆~hdong线87杆 | hdong线86杆 | hdong线87杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 96 | hdong线78杆~hdong线79杆 | hdong线78杆 | hdong线79杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 97 | hdong线汇龙支线04杆~hdong线汇龙支线05杆 | hdong线汇龙支线04杆 | hdong线汇龙支线05杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 98 | hdong线张村2#变支线11杆~hdong线张村2#变支线12杆 | hdong线张村2#变支线11杆 | hdong线张村2#变支线12杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 99 | hdong线张村2#变支线17杆~hdong线张村2#变支线18杆 | hdong线张村2#变支线17杆 | hdong线张村2#变支线18杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 100 | hdong线汇龙支线07杆~hdong线汇龙支线08杆 | hdong线汇龙支线07杆 | hdong线汇龙支线08杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 101 | hdong线44杆~hdong线45杆 | hdong线44杆 | hdong线45杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 102 | hdong线张村2#变支线03杆~hdong线张村2#变支线04杆 | hdong线张村2#变支线03杆 | hdong线张村2#变支线04杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 103 | hdong线张村2#变支线06杆~hdong线张村2#变支线07杆 | hdong线张村2#变支线06杆 | hdong线张村2#变支线07杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 104 | hdong线25杆~hdong线26杆 | hdong线25杆 | hdong线26杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 105 | hdong线张村2#变支线13杆~hdong线张村2#变支线14杆 | hdong线张村2#变支线13杆 | hdong线张村2#变支线14杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 106 | hdong线8杆~hdong线9杆 | hdong线8杆 | hdong线9杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 107 | hdong线汇龙支线05杆~hdong线汇龙支线06杆 | hdong线汇龙支线05杆 | hdong线汇龙支线06杆 | 50 | JL(GD)/GIA-240/40 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 108 | hdong线5杆~李口八队电站支线01 | hdong线5杆 | 李口八队电站支线01 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 109 | hdong线74-03杆~hdong线74-04杆 | hdong线74-03杆 | hdong线74-04杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 110 | hdong线12杆~hdong线13杆 | hdong线12杆 | hdong线13杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 111 | hdong线39杆~hdong线40杆 | hdong线39杆 | hdong线40杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 112 | hdong线72杆~hdong线73杆 | hdong线72杆 | hdong线73杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 113 | hdong线50杆~hdong线51杆 | hdong线50杆 | hdong线51杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 114 | hdong线51杆~hdong线52杆 | hdong线51杆 | hdong线52杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 115 | hdong线60杆~hdong线61杆 | hdong线60杆 | hdong线61杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 116 | hdong线49杆~hdong线50杆 | hdong线49杆 | hdong线50杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 117 | 河镇线hdong48杆~hdong线49杆 | 河镇线hdong48杆 | hdong线49杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 118 | hdong线47杆~河镇线hdong48杆 | hdong线47杆 | 河镇线hdong48杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 119 | hdong线59杆~hdong线60杆 | hdong线59杆 | hdong线60杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 120 | 勤丰纺织支线11杆~勤丰纺织支线12杆 | 勤丰纺织支线11杆 | 勤丰纺织支线12杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 121 | 勤丰纺织支线10杆~勤丰纺织支线11杆 | 勤丰纺织支线10杆 | 勤丰纺织支线11杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 122 | 勤丰纺织支线08杆~勤丰纺织支线09杆 | 勤丰纺织支线08杆 | 勤丰纺织支线09杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 123 | 勤丰纺织支线09杆~勤丰纺织支线10杆 | 勤丰纺织支线09杆 | 勤丰纺织支线10杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 124 | hdong线74杆~勤丰纺织支线01杆 | hdong线74杆 | 勤丰纺织支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 125 | 勤丰纺织支线01杆~勤丰纺织支线02杆 | 勤丰纺织支线01杆 | 勤丰纺织支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 126 | 勤丰纺织支线02杆~勤丰纺织支线03杆 | 勤丰纺织支线02杆 | 勤丰纺织支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 127 | 勤丰纺织支线03杆~勤丰纺织支线04杆 | 勤丰纺织支线03杆 | 勤丰纺织支线04杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 128 | 勤丰纺织支线04杆~勤丰纺织支线05杆 | 勤丰纺织支线04杆 | 勤丰纺织支线05杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 129 | hdong线79杆~hdong线80杆 | hdong线79杆 | hdong线80杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 130 | hdong线80杆~hdong线81杆 | hdong线80杆 | hdong线81杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 131 | hdong线74杆~hdong线75杆 | hdong线74杆 | hdong线75杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 132 | 河镇线hdong42杆~hdong线43杆 | 河镇线hdong42杆 | hdong线43杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 133 | hdong线75杆~hdong线76杆 | hdong线75杆 | hdong线76杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 134 | hdong线76杆~hdong线77杆 | hdong线76杆 | hdong线77杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 135 | hdong线77杆~hdong线78杆 | hdong线77杆 | hdong线78杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 136 | 河湾1#支线15杆~河湾1#支线16杆 | 河湾1#支线15杆 | 河湾1#支线16杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 137 | 河湾1#支线16杆~河湾1#支线17杆 | 河湾1#支线16杆 | 河湾1#支线17杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 138 | 河湾1#支线17杆~河湾1#支线18杆 | 河湾1#支线17杆 | 河湾1#支线18杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 139 | 河湾1#支线18杆~河湾1#支线19杆 | 河湾1#支线18杆 | 河湾1#支线19杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 140 | 河湾1#支线19杆~河湾1#支线20杆 | 河湾1#支线19杆 | 河湾1#支线20杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 141 | 河湾1#支线20杆~河湾1#支线21杆 | 河湾1#支线20杆 | 河湾1#支线21杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 142 | 河湾1#支线21杆~河湾1#支线22杆 | 河湾1#支线21杆 | 河湾1#支线22杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 143 | 河湾1#支线22杆~河湾1#支线23杆 | 河湾1#支线22杆 | 河湾1#支线23杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 144 | hdong线74-01杆~hdong线74-02杆 | hdong线74-01杆 | hdong线74-02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 145 | hdong线46杆~hdong线47杆 | hdong线46杆 | hdong线47杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 146 | hdong线24杆~hdong线25杆 | hdong线24杆 | hdong线25杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 147 | hdong线张村2#变支线07杆~hdong线张村2#变支线08杆 | hdong线张村2#变支线07杆 | hdong线张村2#变支线08杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 148 | hdong线20杆~hdong线21杆 | hdong线20杆 | hdong线21杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 149 | hdong线33杆~hdong线34杆 | hdong线33杆 | hdong线34杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 150 | hdong线38杆~hdong线39杆 | hdong线38杆 | hdong线39杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 151 | hdong线35杆~hdong线36杆 | hdong线35杆 | hdong线36杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 152 | hdong线36杆~hdong线37杆 | hdong线36杆 | hdong线37杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 153 | hdong线34杆~hdong线35杆 | hdong线34杆 | hdong线35杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 154 | hdong线66杆~hdong线67杆 | hdong线66杆 | hdong线67杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 155 | hdong线67杆~hdong线68杆 | hdong线67杆 | hdong线68杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 156 | hdong线68杆~hdong线69杆 | hdong线68杆 | hdong线69杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 157 | 勤丰纺织支线05杆~勤丰纺织支线06杆 | 勤丰纺织支线05杆 | 勤丰纺织支线06杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 158 | 勤丰纺织支线06杆~勤丰纺织支线07杆 | 勤丰纺织支线06杆 | 勤丰纺织支线07杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 159 | 勤丰纺织支线07杆~勤丰纺织支线08杆 | 勤丰纺织支线07杆 | 勤丰纺织支线08杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 160 | 河镇线hdong42杆~hdong线张村2#变支线01杆 | 河镇线hdong42杆 | hdong线张村2#变支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 161 | hdong线张村2#变支线01杆~hdong线张村2#变支线02杆 | hdong线张村2#变支线01杆 | hdong线张村2#变支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 162 | hdong线45杆~hdong线46杆 | hdong线45杆 | hdong线46杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 163 | 河湾1#支线02杆~河湾1#支线03杆 | 河湾1#支线02杆 | 河湾1#支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 164 | 河湾1#支线03杆~河湾1#支线04杆 | 河湾1#支线03杆 | 河湾1#支线04杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 165 | 河湾1#支线04杆~河湾1#支线05杆 | 河湾1#支线04杆 | 河湾1#支线05杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 166 | hdong线74-02杆~hdong线74-03杆 | hdong线74-02杆 | hdong线74-03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 167 | 勤丰纺织支线04杆~宏达支01 | 勤丰纺织支线04杆 | 宏达支01 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 168 | 华运蒜业支线01杆~华运蒜业支线02杆 | 华运蒜业支线01杆 | 华运蒜业支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 169 | hdong线74杆~hdong线74-01杆 | hdong线74杆 | hdong线74-01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 170 | hdong线89杆~hdong线90杆 | hdong线89杆 | hdong线90杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 171 | 河湾1#支线05杆~河湾1#支线06杆 | 河湾1#支线05杆 | 河湾1#支线06杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 172 | 河湾1#支线06杆~河湾1#支线07杆 | 河湾1#支线06杆 | 河湾1#支线07杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 173 | 河湾1#支线07杆~河湾1#支线08杆 | 河湾1#支线07杆 | 河湾1#支线08杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 174 | 河湾1#支线08杆~河湾1#支线09杆 | 河湾1#支线08杆 | 河湾1#支线09杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 175 | 勤丰纺织支线12杆~勤丰纺织支线13杆 | 勤丰纺织支线12杆 | 勤丰纺织支线13杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 176 | 勤丰纺织支线13杆~勤丰纺织支线14杆 | 勤丰纺织支线13杆 | 勤丰纺织支线14杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 177 | hdong支线01杆~hdong支线02杆 | hdong支线01杆 | hdong支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 178 | hdong支线02杆~hdong支线03杆 | hdong支线02杆 | hdong支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 179 | hdong支线01杆~3队电站支01 | hdong支线01杆 | 3队电站支01 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 180 | hdong线47杆~河湾四队电站支01 | hdong线47杆 | 河湾四队电站支01 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 181 | 河湾1#支线01杆~河湾1#支线02杆 | 河湾1#支线01杆 | 河湾1#支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 182 | hdong线90杆~hdong线91杆 | hdong线90杆 | hdong线91杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 183 | hdong线91杆~hdong线92杆 | hdong线91杆 | hdong线92杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 184 | hdong线88杆~hdong线89杆 | hdong线88杆 | hdong线89杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 185 | hdong线87杆~hdong线88杆 | hdong线87杆 | hdong线88杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 186 | 河湾1#支线13杆~河湾1#支线14杆 | 河湾1#支线13杆 | 河湾1#支线14杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 187 | 恒东房地产二支线01杆~恒东房地产二支线02杆 | 恒东房地产二支线01杆 | 恒东房地产二支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 188 | 恒东房地产支线01杆~恒东房地产支线02杆 | 恒东房地产支线01杆 | 恒东房地产支线02杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 189 | hdong线张村2#变支线06杆~恒东房地产二支线01杆 | hdong线张村2#变支线06杆 | 恒东房地产二支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 190 | 煤球厂支线05杆~煤球厂支线06杆 | 煤球厂支线05杆 | 煤球厂支线06杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 191 | hdong线38杆~恒东房地产支线01杆 | hdong线38杆 | 恒东房地产支线01杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 192 | 煤球厂支线04杆~煤球厂支线05杆 | 煤球厂支线04杆 | 煤球厂支线05杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 193 | 恒东房地产支线02杆~恒东房地产支线03杆 | 恒东房地产支线02杆 | 恒东房地产支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 194 | 恒东房地产二支线02杆~恒东房地产二支线03杆 | 恒东房地产二支线02杆 | 恒东房地产二支线03杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 195 | hdong线12-1~hdong线12杆 | hdong线12-1 | hdong线12杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hdong | 河东线 | PZXL-00154 | 河湾变 | 196 | hdong线汇龙支线09杆~hdong线汇龙支线10杆 | hdong线汇龙支线09杆 | hdong线汇龙支线10杆 | 50 | JKLGYJ-240 | 邳州_10kV河东线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 2 | hpao线盛川支线1杆~hpao线盛川支线2杆 | hpao线盛川支线1杆 | hpao线盛川支线2杆 | 50 | JKLYJ/QN-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 3 | hpao线墩既村高坡塑料颗粒产支线06杆~hpao线墩既村高坡塑料颗粒产支线07杆 | hpao线墩既村高坡塑料颗粒产支线06杆 | hpao线墩既村高坡塑料颗粒产支线07杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 4 | hpao线32杆~hpao线33杆 | hpao线32杆 | hpao线33杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 5 | hpao线02杆~hpao线03杆 | hpao线02杆 | hpao线03杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 6 | hpao线06杆~hpao线07杆 | hpao线06杆 | hpao线07杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 7 | hpao线16杆~hpao线17杆 | hpao线16杆 | hpao线17杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 8 | hpao线18杆~hpao线19杆 | hpao线18杆 | hpao线19杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 9 | hpao线29杆~hpao线30杆 | hpao线29杆 | hpao线30杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 10 | hpao线05杆~hpao线06杆 | hpao线05杆 | hpao线06杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 11 | hpao线08杆~hpao线09杆 | hpao线08杆 | hpao线09杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 12 | hpao线28杆~hpao线29杆 | hpao线28杆 | hpao线29杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 13 | hpao线23杆~hpao线24杆 | hpao线23杆 | hpao线24杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 14 | hpao线30杆~hpao线31杆 | hpao线30杆 | hpao线31杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 15 | hpao线墩既村高坡塑料颗粒产支线02杆~hpao线墩既村高坡塑料颗粒产支线03杆 | hpao线墩既村高坡塑料颗粒产支线02杆 | hpao线墩既村高坡塑料颗粒产支线03杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 16 | hpao线34杆~hpao线35杆 | hpao线34杆 | hpao线35杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 17 | hpao线40杆~hpao线41杆 | hpao线40杆 | hpao线41杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 18 | hpao线03杆~hpao线04杆 | hpao线03杆 | hpao线04杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 19 | hpao线墩既村高坡塑料颗粒产支线03杆~hpao线墩既村高坡塑料颗粒产支线04杆 | hpao线墩既村高坡塑料颗粒产支线03杆 | hpao线墩既村高坡塑料颗粒产支线04杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 20 | hpao线19杆~hpao线20杆 | hpao线19杆 | hpao线20杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 21 | hpao线33杆~hpao线34杆 | hpao线33杆 | hpao线34杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 22 | hpao线38杆~hpao线39杆 | hpao线38杆 | hpao线39杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 23 | hpao线58杆~hpao线59杆 | hpao线58杆 | hpao线59杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 24 | hpao线57杆~hpao线58杆 | hpao线57杆 | hpao线58杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 25 | hpao线51杆~hpao线52杆 | hpao线51杆 | hpao线52杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 26 | hpao线50杆~hpao线51杆 | hpao线50杆 | hpao线51杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 27 | hpao线52杆~hpao线53杆 | hpao线52杆 | hpao线53杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 28 | hpao线56杆~hpao线57杆 | hpao线56杆 | hpao线57杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 29 | hpao线49杆~hpao线50杆 | hpao线49杆 | hpao线50杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 30 | hpao线55杆~hpao线56杆 | hpao线55杆 | hpao线56杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 31 | hpao线53杆~hpao线54杆 | hpao线53杆 | hpao线54杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 32 | hpao线墩既村高坡塑料颗粒产支线01杆~hpao线墩既村高坡塑料颗粒产支线02杆 | hpao线墩既村高坡塑料颗粒产支线01杆 | hpao线墩既村高坡塑料颗粒产支线02杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 33 | hpao线09杆~hpao线10杆 | hpao线09杆 | hpao线10杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 34 | hpao线35杆~hpao线36杆 | hpao线35杆 | hpao线36杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 35 | hpao线37杆~hpao线38杆 | hpao线37杆 | hpao线38杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 36 | hpao线14杆~hpao线15杆 | hpao线14杆 | hpao线15杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 37 | hpao线13杆~hpao线14杆 | hpao线13杆 | hpao线14杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 38 | hpao线48杆~hpao线49杆 | hpao线48杆 | hpao线49杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 39 | hpao线47杆~hpao线48杆 | hpao线47杆 | hpao线48杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 40 | hpao线44杆~hpao线45杆 | hpao线44杆 | hpao线45杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 41 | hpao线46杆~hpao线47杆 | hpao线46杆 | hpao线47杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 42 | hpao线45杆~hpao线46杆 | hpao线45杆 | hpao线46杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 43 | hpao线54杆~hpao线55杆 | hpao线54杆 | hpao线55杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 44 | hpao线15杆~hpao线16杆 | hpao线15杆 | hpao线16杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 45 | hpao线21杆~hpao线22杆 | hpao线21杆 | hpao线22杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 46 | hpao线22杆~hpao线23杆 | hpao线22杆 | hpao线23杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 47 | hpao线31杆~hpao线32杆 | hpao线31杆 | hpao线32杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 48 | hpao线11杆~hpao线12杆 | hpao线11杆 | hpao线12杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 49 | hpao线27杆~hpao线28杆 | hpao线27杆 | hpao线28杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 50 | hpao线07杆~hpao线08杆 | hpao线07杆 | hpao线08杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 51 | hpao线26杆~hpao线27杆 | hpao线26杆 | hpao线27杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 52 | hpao线04杆~hpao线05杆 | hpao线04杆 | hpao线05杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 53 | hpao线墩既村高坡塑料颗粒产支线05杆~hpao线墩既村高坡塑料颗粒产支线06杆 | hpao线墩既村高坡塑料颗粒产支线05杆 | hpao线墩既村高坡塑料颗粒产支线06杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 54 | hpao线24杆~hpao线25杆 | hpao线24杆 | hpao线25杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 55 | hpao线39杆~hpao线40杆 | hpao线39杆 | hpao线40杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 56 | hpao线01杆~hpao线02杆 | hpao线01杆 | hpao线02杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 57 | hpao线20杆~hpao线21杆 | hpao线20杆 | hpao线21杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 58 | hpao线41杆~hpao线42杆 | hpao线41杆 | hpao线42杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 59 | hpao线17杆~hpao线18杆 | hpao线17杆 | hpao线18杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 60 | hpao线25杆~hpao线26杆 | hpao线25杆 | hpao线26杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 61 | hpao线10杆~hpao线11杆 | hpao线10杆 | hpao线11杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 62 | hpao线12杆~hpao线13杆 | hpao线12杆 | hpao线13杆 | 50 | LGJ-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 63 | hpao线墩既村高坡塑料颗粒产支线04杆~hpao线墩既村高坡塑料颗粒产支线05杆 | hpao线墩既村高坡塑料颗粒产支线04杆 | hpao线墩既村高坡塑料颗粒产支线05杆 | 50 | JKLYJ-150 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 64 | hpao线盛川支线4杆~hpao线盛川支线5杆 | hpao线盛川支线4杆 | hpao线盛川支线5杆 | 50 | JKLYJ/QN-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 65 | hpao线52杆~hpao线盛川支线1杆 | hpao线52杆 | hpao线盛川支线1杆 | 50 | JKLYJ/QN-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 66 | hpao线盛川支线2杆~hpao线盛川支线3杆 | hpao线盛川支线2杆 | hpao线盛川支线3杆 | 50 | JKLYJ/QN-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 67 | hpao线盛川支线3杆~hpao线盛川支线4杆 | hpao线盛川支线3杆 | hpao线盛川支线4杆 | 50 | JKLYJ/QN-10-240 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 68 | hpao线王场湖支线1杆~hpao线王场湖支线2杆 | hpao线王场湖支线1杆 | hpao线王场湖支线2杆 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 69 | hpao线墩既村高坡塑料颗粒产支线10~hpao线墩既村高坡塑料颗粒产支线11 | hpao线墩既村高坡塑料颗粒产支线10 | hpao线墩既村高坡塑料颗粒产支线11 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 70 | hpao线墩既村高坡塑料颗粒产支线9~hpao线墩既村高坡塑料颗粒产支线10 | hpao线墩既村高坡塑料颗粒产支线9 | hpao线墩既村高坡塑料颗粒产支线10 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 71 | hpao线43杆~hpao线王场湖排灌站支线1杆 | hpao线43杆 | hpao线王场湖排灌站支线1杆 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 72 | hpao线墩既村高坡塑料颗粒产支线8~hpao线墩既村高坡塑料颗粒产支线9 | hpao线墩既村高坡塑料颗粒产支线8 | hpao线墩既村高坡塑料颗粒产支线9 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hpao | 河炮线 | PZXL-00161 | 河湾变 | 73 | hpao线墩既村高坡塑料颗粒产支线07杆~hpao线墩既村高坡塑料颗粒产支线8 | hpao线墩既村高坡塑料颗粒产支线07杆 | hpao线墩既村高坡塑料颗粒产支线8 | 50 | JL/G1A-240/30 | 邳州_10kV河炮线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 2 | 10kVhzhen线56#杆~hzhen线56-1 | 10kVhzhen线56#杆 | hzhen线56-1 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 3 | 张村1变支线33杆~张村1变支线34杆 | 张村1变支线33杆 | 张村1变支线34杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 4 | 张村1变支线35杆~张村1变支线36杆 | 张村1变支线35杆 | 张村1变支线36杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 5 | 张村1变支线32杆~张村1变支线33杆 | 张村1变支线32杆 | 张村1变支线33杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 6 | 张村1变支线36杆~张村1变支线37杆 | 张村1变支线36杆 | 张村1变支线37杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 7 | 张村1变支线34杆~张村1变支线35杆 | 张村1变支线34杆 | 张村1变支线35杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 8 | 张村1变支线37杆~张村1变支线38杆 | 张村1变支线37杆 | 张村1变支线38杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 9 | 10kVhzhen线01#杆~10kVhzhen线02#杆 | 10kVhzhen线01#杆 | 10kVhzhen线02#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10 | 10kVhzhen线61#杆~10kVhzhen线62#杆 | 10kVhzhen线61#杆 | 10kVhzhen线62#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 11 | 南方永磁支线8杆~南方永磁支线9杆 | 南方永磁支线8杆 | 南方永磁支线9杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 12 | 南方永磁支线12杆~南方永磁支线13杆 | 南方永磁支线12杆 | 南方永磁支线13杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 13 | 南方永磁支线18杆~南方永磁支线19杆 | 南方永磁支线18杆 | 南方永磁支线19杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 14 | 南方永磁支线4杆~南方永磁支线5杆 | 南方永磁支线4杆 | 南方永磁支线5杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 15 | 南方永磁支线15杆~南方永磁支线16杆 | 南方永磁支线15杆 | 南方永磁支线16杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 16 | 南方永磁支线16杆~南方永磁支线17杆 | 南方永磁支线16杆 | 南方永磁支线17杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 17 | 南方永磁支线11杆~南方永磁支线12杆 | 南方永磁支线11杆 | 南方永磁支线12杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 18 | 南方永磁支线9杆~南方永磁支线10杆 | 南方永磁支线9杆 | 南方永磁支线10杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 19 | 南方永磁支线7杆~南方永磁支线8杆 | 南方永磁支线7杆 | 南方永磁支线8杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 20 | 南方永磁支线2杆~南方永磁支线3杆 | 南方永磁支线2杆 | 南方永磁支线3杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 21 | 南方永磁支线5杆~南方永磁支线6杆 | 南方永磁支线5杆 | 南方永磁支线6杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 22 | 10kVhzhen线93杆~南方永磁支线1杆 | 10kVhzhen线93杆 | 南方永磁支线1杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 23 | 南方永磁支线17杆~南方永磁支线18杆 | 南方永磁支线17杆 | 南方永磁支线18杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 24 | 南方永磁支线6杆~南方永磁支线7杆 | 南方永磁支线6杆 | 南方永磁支线7杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 25 | 南方永磁支线3杆~南方永磁支线4杆 | 南方永磁支线3杆 | 南方永磁支线4杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 26 | 南方永磁支线14杆~南方永磁支线15杆 | 南方永磁支线14杆 | 南方永磁支线15杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 27 | 南方永磁支线13杆~南方永磁支线14杆 | 南方永磁支线13杆 | 南方永磁支线14杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 28 | 南方永磁支线10杆~南方永磁支线11杆 | 南方永磁支线10杆 | 南方永磁支线11杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 29 | 南方永磁支线1杆~南方永磁支线2杆 | 南方永磁支线1杆 | 南方永磁支线2杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 30 | 文苑路支线26杆~文苑路支线27杆 | 文苑路支线26杆 | 文苑路支线27杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 31 | 文苑路支线21杆~文苑路支线22杆 | 文苑路支线21杆 | 文苑路支线22杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 32 | 文苑路支线24杆~文苑路支线25杆 | 文苑路支线24杆 | 文苑路支线25杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 33 | 文苑路支线8杆~文苑路支线9杆 | 文苑路支线8杆 | 文苑路支线9杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 34 | 文苑路支线1杆~文苑路支线2杆 | 文苑路支线1杆 | 文苑路支线2杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 35 | 文苑路支线5杆~文苑路支线6杆 | 文苑路支线5杆 | 文苑路支线6杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 36 | 文苑路支线11杆~文苑路支线12杆 | 文苑路支线11杆 | 文苑路支线12杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 37 | 文苑路支线10杆~文苑路支线11杆 | 文苑路支线10杆 | 文苑路支线11杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 38 | 文苑路支线23杆~文苑路支线24杆 | 文苑路支线23杆 | 文苑路支线24杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 39 | 文苑路支线6杆~文苑路支线7杆 | 文苑路支线6杆 | 文苑路支线7杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 40 | 文苑路支线7杆~文苑路支线8杆 | 文苑路支线7杆 | 文苑路支线8杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 41 | 文苑路支线18杆~文苑路支线19杆 | 文苑路支线18杆 | 文苑路支线19杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 42 | 文苑路支线2杆~文苑路支线3杆 | 文苑路支线2杆 | 文苑路支线3杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 43 | 文苑路支线20杆~文苑路支线21杆 | 文苑路支线20杆 | 文苑路支线21杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 44 | 文苑路支线4杆~文苑路支线5杆 | 文苑路支线4杆 | 文苑路支线5杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 45 | 文苑路支线16杆~文苑路支线17杆 | 文苑路支线16杆 | 文苑路支线17杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 46 | 文苑路支线13杆~文苑路支线14杆 | 文苑路支线13杆 | 文苑路支线14杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 47 | 文苑路支线9杆~文苑路支线10杆 | 文苑路支线9杆 | 文苑路支线10杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 48 | 文苑路支线14杆~文苑路支线15杆 | 文苑路支线14杆 | 文苑路支线15杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 49 | 文苑路支线22杆~文苑路支线23杆 | 文苑路支线22杆 | 文苑路支线23杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 50 | 文苑路支线3杆~文苑路支线4杆 | 文苑路支线3杆 | 文苑路支线4杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 51 | 10kVhzhen线49#杆~文苑路支线1杆 | 10kVhzhen线49#杆 | 文苑路支线1杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 52 | 文苑路支线29杆~文苑路支线30杆 | 文苑路支线29杆 | 文苑路支线30杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 53 | 文苑路支线19杆~文苑路支线20杆 | 文苑路支线19杆 | 文苑路支线20杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 54 | 文苑路支线17杆~文苑路支线18杆 | 文苑路支线17杆 | 文苑路支线18杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 55 | 文苑路支线27杆~文苑路支线28杆 | 文苑路支线27杆 | 文苑路支线28杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 56 | 文苑路支线25杆~文苑路支线26杆 | 文苑路支线25杆 | 文苑路支线26杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 57 | 文苑路支线28杆~文苑路支线29杆 | 文苑路支线28杆 | 文苑路支线29杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 58 | 文苑路支线12杆~文苑路支线13杆 | 文苑路支线12杆 | 文苑路支线13杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 59 | 文苑路支线15杆~文苑路支线16杆 | 文苑路支线15杆 | 文苑路支线16杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 60 | 10kVhzhen线40#杆~工业园区支线01杆 | 10kVhzhen线40#杆 | 工业园区支线01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 61 | 10kVhzhen线37#杆~10kVhzhen线38#杆 | 10kVhzhen线37#杆 | 10kVhzhen线38#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 62 | 工业园区支线12杆~工业园区支线13杆 | 工业园区支线12杆 | 工业园区支线13杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 63 | 10kVhzhen线05#杆~10kVhzhen线06#杆 | 10kVhzhen线05#杆 | 10kVhzhen线06#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 64 | 工业园区支线15杆~工业园区支线16杆 | 工业园区支线15杆 | 工业园区支线16杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 65 | 工业园区支线01杆~工业园区支线02杆 | 工业园区支线01杆 | 工业园区支线02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 66 | 10kVhzhen线48#杆~10kVhzhen线49#杆 | 10kVhzhen线48#杆 | 10kVhzhen线49#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 67 | 10kVhzhen线13#杆~10kVhzhen线14#杆 | 10kVhzhen线13#杆 | 10kVhzhen线14#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 68 | 工业园区支线04杆~工业园区支线05杆 | 工业园区支线04杆 | 工业园区支线05杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 69 | 10kVhzhen线11#杆~10kVhzhen线12#杆 | 10kVhzhen线11#杆 | 10kVhzhen线12#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 70 | 10kVhzhen线12#杆~10kVhzhen线13#杆 | 10kVhzhen线12#杆 | 10kVhzhen线13#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 71 | 张村10变支线05杆~张村10变支线06杆 | 张村10变支线05杆 | 张村10变支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 72 | 张村10变支线06杆~张村10变支线07杆 | 张村10变支线06杆 | 张村10变支线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 73 | 张村10变支线07杆~张村10变支线08杆 | 张村10变支线07杆 | 张村10变支线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 74 | 张村1变支线30杆~张村1变支线31杆 | 张村1变支线30杆 | 张村1变支线31杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 75 | 张村1变支线29杆~张村1变支线30杆 | 张村1变支线29杆 | 张村1变支线30杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 76 | 张村1变支线31杆~张村1变支线32杆 | 张村1变支线31杆 | 张村1变支线32杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 77 | 10kVhzhen线74杆~10kVhzhen线75杆 | 10kVhzhen线74杆 | 10kVhzhen线75杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 78 | 10kVhzhen线75杆~10kVhzhen线76杆 | 10kVhzhen线75杆 | 10kVhzhen线76杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 79 | 工业园区支线07杆~工业园区支线08杆 | 工业园区支线07杆 | 工业园区支线08杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 80 | 张村1变支线28杆~张村1变支线29杆 | 张村1变支线28杆 | 张村1变支线29杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 81 | 张村1变支线14杆~运河张村11变支线01杆 | 张村1变支线14杆 | 运河张村11变支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 82 | 张村1变支线23杆~张村1变支线24杆 | 张村1变支线23杆 | 张村1变支线24杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 83 | 张村10变支线04杆~张村10变支线05杆 | 张村10变支线04杆 | 张村10变支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 84 | 张村1变支线14杆~张村1变支线15杆 | 张村1变支线14杆 | 张村1变支线15杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 85 | 张村1变支线26杆~张村1变支线27杆 | 张村1变支线26杆 | 张村1变支线27杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 86 | 张村10变支线03杆~张村10变支线04杆 | 张村10变支线03杆 | 张村10变支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 87 | 张村1变支线20杆~张村10变支线01杆 | 张村1变支线20杆 | 张村10变支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 88 | 张村1变支线16杆~张村1变支线17杆 | 张村1变支线16杆 | 张村1变支线17杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 89 | 张村10变支线01杆~张村10变支线02杆 | 张村10变支线01杆 | 张村10变支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 90 | 张村1变支线19杆~张村1变支线20杆 | 张村1变支线19杆 | 张村1变支线20杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 91 | 张村1变支线17杆~张村1变支线18杆 | 张村1变支线17杆 | 张村1变支线18杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 92 | 张村1变支线18杆~张村1变支线19杆 | 张村1变支线18杆 | 张村1变支线19杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 93 | 张村1变支线15杆~张村1变支线16杆 | 张村1变支线15杆 | 张村1变支线16杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 94 | 张村1变支线20杆~张村1变支线21杆 | 张村1变支线20杆 | 张村1变支线21杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 95 | 张村1变支线01杆~张村1变支线02杆 | 张村1变支线01杆 | 张村1变支线02杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 96 | 张村1变支线03杆~张村1变支线04杆 | 张村1变支线03杆 | 张村1变支线04杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 97 | 张村1变支线04杆~张村1变支线05杆 | 张村1变支线04杆 | 张村1变支线05杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 98 | 张村1变支线05杆~张村1变支线06杆 | 张村1变支线05杆 | 张村1变支线06杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 99 | 张村1变支线06杆~张村1变支线07杆 | 张村1变支线06杆 | 张村1变支线07杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 100 | 张村1变支线08杆~张村1变支线09杆 | 张村1变支线08杆 | 张村1变支线09杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 101 | 张村1变支线09杆~张村1变支线10杆 | 张村1变支线09杆 | 张村1变支线10杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 102 | 张村10变支线02杆~张村10变支线03杆 | 张村10变支线02杆 | 张村10变支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 103 | 张村1变支线21杆~张村1变支线22杆 | 张村1变支线21杆 | 张村1变支线22杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 104 | 张村1变支线22杆~张村1变支线23杆 | 张村1变支线22杆 | 张村1变支线23杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 105 | 张村1变支线24杆~张村1变支线25杆 | 张村1变支线24杆 | 张村1变支线25杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 106 | 张村1变支线25杆~张村1变支线26杆 | 张村1变支线25杆 | 张村1变支线26杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 107 | 张村1变支线27杆~张村1变支线28杆 | 张村1变支线27杆 | 张村1变支线28杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 108 | 张村1变支线10杆~张村1变支线11杆 | 张村1变支线10杆 | 张村1变支线11杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 109 | 张村1变支线11杆~张村1变支线12杆 | 张村1变支线11杆 | 张村1变支线12杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 110 | 张村1变支线12杆~张村1变支线13杆 | 张村1变支线12杆 | 张村1变支线13杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 111 | 张村1变支线13杆~张村1变支线14杆 | 张村1变支线13杆 | 张村1变支线14杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 112 | 张村1变支线07杆~张村1变支线08杆 | 张村1变支线07杆 | 张村1变支线08杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 113 | 10kVhzhen线83杆~张村1变支线01杆 | 10kVhzhen线83杆 | 张村1变支线01杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 114 | 张村1变支线02杆~张村1变支线03杆 | 张村1变支线02杆 | 张村1变支线03杆 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 115 | 张村1变支线04杆~河湾4＃变支01 | 张村1变支线04杆 | 河湾4＃变支01 | 50 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 116 | 10kVhzhen线21#杆~看守所支线01杆 | 10kVhzhen线21#杆 | 看守所支线01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 117 | 看守所支线07杆~看守所支线08杆 | 看守所支线07杆 | 看守所支线08杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 118 | 10kVhzhen线43#杆~10kVhzhen线44#杆 | 10kVhzhen线43#杆 | 10kVhzhen线44#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 119 | 10kVhzhen线47#杆~10kVhzhen线48#杆 | 10kVhzhen线47#杆 | 10kVhzhen线48#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 120 | 看守所支线06杆~看守所支线07杆 | 看守所支线06杆 | 看守所支线07杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 121 | 10kVhzhen线28#杆~10kVhzhen线29#杆 | 10kVhzhen线28#杆 | 10kVhzhen线29#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 122 | 工业园区支线16杆~工业园区支线17杆 | 工业园区支线16杆 | 工业园区支线17杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 123 | 10kVhzhen线34#杆~10kVhzhen线35#杆 | 10kVhzhen线34#杆 | 10kVhzhen线35#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 124 | 10kVhzhen线46#杆~10kVhzhen线47#杆 | 10kVhzhen线46#杆 | 10kVhzhen线47#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 125 | 10kVhzhen线16#杆~10kVhzhen线17#杆 | 10kVhzhen线16#杆 | 10kVhzhen线17#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 126 | 10kVhzhen线27#杆~10kVhzhen线28#杆 | 10kVhzhen线27#杆 | 10kVhzhen线28#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 127 | 10kVhzhen线29#杆~10kVhzhen线30#杆 | 10kVhzhen线29#杆 | 10kVhzhen线30#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 128 | hzhen线45杆~10kVhzhen线46#杆 | hzhen线45杆 | 10kVhzhen线46#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 129 | 看守所支线03杆~看守所支线04杆 | 看守所支线03杆 | 看守所支线04杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 130 | 10kVhzhen线42#杆~10kVhzhen线43#杆 | 10kVhzhen线42#杆 | 10kVhzhen线43#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 131 | 工业园区支线03杆~欢乐买支线01杆 | 工业园区支线03杆 | 欢乐买支线01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 132 | 10kVhzhen线18#杆~10kVhzhen线19#杆 | 10kVhzhen线18#杆 | 10kVhzhen线19#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 133 | 10kVhzhen线23#杆~10kVhzhen线24#杆 | 10kVhzhen线23#杆 | 10kVhzhen线24#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 134 | 10kVhzhen线21#杆~10kVhzhen线22#杆 | 10kVhzhen线21#杆 | 10kVhzhen线22#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 135 | 工业园区支线10杆~工业园区支线11杆 | 工业园区支线10杆 | 工业园区支线11杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 136 | 10kVhzhen线20#杆~10kVhzhen线21#杆 | 10kVhzhen线20#杆 | 10kVhzhen线21#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 137 | 10kVhzhen线39#杆~10kVhzhen线40#杆 | 10kVhzhen线39#杆 | 10kVhzhen线40#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 138 | 看守所支线05杆~看守所支线06杆 | 看守所支线05杆 | 看守所支线06杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 139 | 10kVhzhen线15#杆~10kVhzhen线16#杆 | 10kVhzhen线15#杆 | 10kVhzhen线16#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 140 | 10kVhzhen线17#杆~10kVhzhen线18#杆 | 10kVhzhen线17#杆 | 10kVhzhen线18#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 141 | 10kVhzhen线26#杆~10kVhzhen线27#杆 | 10kVhzhen线26#杆 | 10kVhzhen线27#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 142 | 工业园区支线02杆~工业园区支线03杆 | 工业园区支线02杆 | 工业园区支线03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 143 | 10kVhzhen线41#杆~10kVhzhen线42#杆 | 10kVhzhen线41#杆 | 10kVhzhen线42#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 144 | 工业园区支线03杆~工业园区支线04杆 | 工业园区支线03杆 | 工业园区支线04杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 145 | 欢乐买支线01杆~欢乐买支线02杆 | 欢乐买支线01杆 | 欢乐买支线02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 146 | 10kVhzhen线14#杆~10kVhzhen线15#杆 | 10kVhzhen线14#杆 | 10kVhzhen线15#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 147 | 10kVhzhen线31#杆~10kVhzhen线32#杆 | 10kVhzhen线31#杆 | 10kVhzhen线32#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 148 | 10kVhzhen线25#杆~10kVhzhen线26#杆 | 10kVhzhen线25#杆 | 10kVhzhen线26#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 149 | 10kVhzhen线03#杆~10kVhzhen线04#杆 | 10kVhzhen线03#杆 | 10kVhzhen线04#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 150 | 10kVhzhen线06#杆~hzhen线07杆 | 10kVhzhen线06#杆 | hzhen线07杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 151 | 工业园区支线17杆~工业园区支线18杆 | 工业园区支线17杆 | 工业园区支线18杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 152 | 工业园区支线06杆~工业园区支线07杆 | 工业园区支线06杆 | 工业园区支线07杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 153 | 10kVhzhen线02#杆~10kVhzhen线03#杆 | 10kVhzhen线02#杆 | 10kVhzhen线03#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 154 | 10kVhzhen线08#杆~10kVhzhen线09#杆 | 10kVhzhen线08#杆 | 10kVhzhen线09#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 155 | 工业园区支线09杆~工业园区支线10杆 | 工业园区支线09杆 | 工业园区支线10杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 156 | 10kVhzhen线38#杆~10kVhzhen线39#杆 | 10kVhzhen线38#杆 | 10kVhzhen线39#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 157 | 10kVhzhen线04#杆~10kVhzhen线05#杆 | 10kVhzhen线04#杆 | 10kVhzhen线05#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 158 | 工业园区支线13杆~工业园区支线14杆 | 工业园区支线13杆 | 工业园区支线14杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 159 | 10kVhzhen线19#杆~10kVhzhen线20#杆 | 10kVhzhen线19#杆 | 10kVhzhen线20#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 160 | 10kVhzhen线30#杆~10kVhzhen线31#杆 | 10kVhzhen线30#杆 | 10kVhzhen线31#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 161 | 10kVhzhen线09#杆~10kVhzhen线10#杆 | 10kVhzhen线09#杆 | 10kVhzhen线10#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 162 | 10kVhzhen线22#杆~10kVhzhen线23#杆 | 10kVhzhen线22#杆 | 10kVhzhen线23#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 163 | 10kVhzhen线33#杆~10kVhzhen线34#杆 | 10kVhzhen线33#杆 | 10kVhzhen线34#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 164 | 10kVhzhen线35#杆~10kVhzhen线36#杆 | 10kVhzhen线35#杆 | 10kVhzhen线36#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 165 | 10kVhzhen线10#杆~10kVhzhen线11#杆 | 10kVhzhen线10#杆 | 10kVhzhen线11#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 166 | 工业园区支线14杆~工业园区支线15杆 | 工业园区支线14杆 | 工业园区支线15杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 167 | 看守所支线04杆~看守所支线05杆 | 看守所支线04杆 | 看守所支线05杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 168 | 10kVhzhen线36#杆~10kVhzhen线37#杆 | 10kVhzhen线36#杆 | 10kVhzhen线37#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 169 | hzhen线07杆~10kVhzhen线08#杆 | hzhen线07杆 | 10kVhzhen线08#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 170 | 10kVhzhen线40#杆~10kVhzhen线41#杆 | 10kVhzhen线40#杆 | 10kVhzhen线41#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 171 | 工业园区支线11杆~工业园区支线12杆 | 工业园区支线11杆 | 工业园区支线12杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 172 | 工业园区支线08杆~工业园区支线09杆 | 工业园区支线08杆 | 工业园区支线09杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 173 | 10kVhzhen线24#杆~10kVhzhen线25#杆 | 10kVhzhen线24#杆 | 10kVhzhen线25#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 174 | 10kVhzhen线44#杆~hzhen线45杆 | 10kVhzhen线44#杆 | hzhen线45杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 175 | 10kVhzhen线32#杆~10kVhzhen线33#杆 | 10kVhzhen线32#杆 | 10kVhzhen线33#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 176 | 看守所支线02杆~看守所支线03杆 | 看守所支线02杆 | 看守所支线03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 177 | hzhen线勤丰纺织支线07杆~hzhen线勤丰纺织支线08杆 | hzhen线勤丰纺织支线07杆 | hzhen线勤丰纺织支线08杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 178 | 10kVhzhen线58#杆~10kVhzhen线59#杆 | 10kVhzhen线58#杆 | 10kVhzhen线59#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 179 | 10kVhzhen线70#杆~10kVhzhen线71#杆 | 10kVhzhen线70#杆 | 10kVhzhen线71#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 180 | 看守所支线05杆~看守所支线3-01杆 | 看守所支线05杆 | 看守所支线3-01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 181 | 10kVhzhen线75-01杆~10kVhzhen线75-02杆 | 10kVhzhen线75-01杆 | 10kVhzhen线75-02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 182 | 欢乐买支线02杆~欢乐买支线03杆 | 欢乐买支线02杆 | 欢乐买支线03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 183 | 10kVhzhen线79杆~垃圾站支线01杆 | 10kVhzhen线79杆 | 垃圾站支线01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 184 | 看守所支线01杆~看守所支线02杆 | 看守所支线01杆 | 看守所支线02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 185 | 10kVhzhen线53#杆~10kVhzhen线54#杆 | 10kVhzhen线53#杆 | 10kVhzhen线54#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 186 | 10kVhzhen线57#杆~10kVhzhen线58#杆 | 10kVhzhen线57#杆 | 10kVhzhen线58#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 187 | 10kVhzhen线56#杆~10kVhzhen线57#杆 | 10kVhzhen线56#杆 | 10kVhzhen线57#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 188 | 垃圾站支线01杆~垃圾站支线02杆 | 垃圾站支线01杆 | 垃圾站支线02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 189 | hzhen线勤丰纺织支线05杆~hzhen线勤丰纺织支线06杆 | hzhen线勤丰纺织支线05杆 | hzhen线勤丰纺织支线06杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 190 | 10kVhzhen线54#杆~10kVhzhen线55#杆 | 10kVhzhen线54#杆 | 10kVhzhen线55#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 191 | 10kVhzhen线75-03杆~10kVhzhen线75-04杆 | 10kVhzhen线75-03杆 | 10kVhzhen线75-04杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 192 | 10kVhzhen线81杆~10kVhzhen线82杆 | 10kVhzhen线81杆 | 10kVhzhen线82杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 193 | 10kVhzhen线80杆~10kVhzhen线81杆 | 10kVhzhen线80杆 | 10kVhzhen线81杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 194 | hzhen线勤丰纺织支线08杆~hzhen线勤丰纺织支线09杆 | hzhen线勤丰纺织支线08杆 | hzhen线勤丰纺织支线09杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 195 | 10kVhzhen线71#杆~10kVhzhen线72#杆 | 10kVhzhen线71#杆 | 10kVhzhen线72#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 196 | 10kVhzhen线59#杆~10kVhzhen线60#杆 | 10kVhzhen线59#杆 | 10kVhzhen线60#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 197 | 10kVhzhen线91杆~10kVhzhen线92杆 | 10kVhzhen线91杆 | 10kVhzhen线92杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 198 | hzhen线勤丰纺织支线06杆~hzhen线勤丰纺织支线07杆 | hzhen线勤丰纺织支线06杆 | hzhen线勤丰纺织支线07杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 199 | 10kVhzhen线50#杆~10kVhzhen线51#杆 | 10kVhzhen线50#杆 | 10kVhzhen线51#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 200 | 10kVhzhen线75杆~hzhen线勤丰纺织支线01杆 | 10kVhzhen线75杆 | hzhen线勤丰纺织支线01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 201 | 10kVhzhen线89杆~10kVhzhen线90杆 | 10kVhzhen线89杆 | 10kVhzhen线90杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 202 | 10kVhzhen线75-04杆~10kVhzhen线75-05杆 | 10kVhzhen线75-04杆 | 10kVhzhen线75-05杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 203 | hzhen线勤丰纺织支线01杆~hzhen线勤丰纺织支线02杆 | hzhen线勤丰纺织支线01杆 | hzhen线勤丰纺织支线02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 204 | 10kVhzhen线62#杆~10kVhzhen线63#杆 | 10kVhzhen线62#杆 | 10kVhzhen线63#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 205 | 10kVhzhen线72#杆~10kVhzhen线73#杆 | 10kVhzhen线72#杆 | 10kVhzhen线73#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 206 | 10kVhzhen线87杆~10kVhzhen线88杆 | 10kVhzhen线87杆 | 10kVhzhen线88杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 207 | 10kVhzhen线86杆~10kVhzhen线87杆 | 10kVhzhen线86杆 | 10kVhzhen线87杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 208 | 10kVhzhen线49#杆~10kVhzhen线50#杆 | 10kVhzhen线49#杆 | 10kVhzhen线50#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 209 | 10kVhzhen线51#杆~10kVhzhen线52#杆 | 10kVhzhen线51#杆 | 10kVhzhen线52#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 210 | 10kVhzhen线84杆~10kVhzhen线85杆 | 10kVhzhen线84杆 | 10kVhzhen线85杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 211 | 看守所支线3-01杆~看守所支线3-02杆 | 看守所支线3-01杆 | 看守所支线3-02杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 212 | 垃圾站支线02杆~垃圾站支线03杆 | 垃圾站支线02杆 | 垃圾站支线03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 213 | hzhen线勤丰纺织支线03杆~hzhen线勤丰纺织支线04杆 | hzhen线勤丰纺织支线03杆 | hzhen线勤丰纺织支线04杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 214 | 10kVhzhen线68#杆~10kVhzhen线69#杆 | 10kVhzhen线68#杆 | 10kVhzhen线69#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 215 | 10kVhzhen线85杆~10kVhzhen线86杆 | 10kVhzhen线85杆 | 10kVhzhen线86杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 216 | 10kVhzhen线77杆~10kVhzhen线78杆 | 10kVhzhen线77杆 | 10kVhzhen线78杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 217 | 10kVhzhen线75-02杆~10kVhzhen线75-03杆 | 10kVhzhen线75-02杆 | 10kVhzhen线75-03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 218 | 10kVhzhen线78杆~10kVhzhen线79杆 | 10kVhzhen线78杆 | 10kVhzhen线79杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 219 | 10kVhzhen线82杆~10kVhzhen线83杆 | 10kVhzhen线82杆 | 10kVhzhen线83杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 220 | 10kVhzhen线52#杆~10kVhzhen线53#杆 | 10kVhzhen线52#杆 | 10kVhzhen线53#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 221 | 10kVhzhen线92杆~10kVhzhen线93杆 | 10kVhzhen线92杆 | 10kVhzhen线93杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 222 | 10kVhzhen线64#杆~10kVhzhen线65#杆 | 10kVhzhen线64#杆 | 10kVhzhen线65#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 223 | 10kVhzhen线60#杆~10kVhzhen线61#杆 | 10kVhzhen线60#杆 | 10kVhzhen线61#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 224 | hzhen线勤丰纺织支线02杆~hzhen线勤丰纺织支线03杆 | hzhen线勤丰纺织支线02杆 | hzhen线勤丰纺织支线03杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 225 | 10kVhzhen线83杆~10kVhzhen线84杆 | 10kVhzhen线83杆 | 10kVhzhen线84杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 226 | 10kVhzhen线55#杆~10kVhzhen线56#杆 | 10kVhzhen线55#杆 | 10kVhzhen线56#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 227 | 10kVhzhen线79杆~10kVhzhen线80杆 | 10kVhzhen线79杆 | 10kVhzhen线80杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 228 | 10kVhzhen线67#杆~10kVhzhen线68#杆 | 10kVhzhen线67#杆 | 10kVhzhen线68#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 229 | 10kVhzhen线76杆~10kVhzhen线77杆 | 10kVhzhen线76杆 | 10kVhzhen线77杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 230 | 垃圾站支线03杆~垃圾站支线04杆 | 垃圾站支线03杆 | 垃圾站支线04杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 231 | 10kVhzhen线69#杆~10kVhzhen线70#杆 | 10kVhzhen线69#杆 | 10kVhzhen线70#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 232 | 10kVhzhen线90杆~10kVhzhen线91杆 | 10kVhzhen线90杆 | 10kVhzhen线91杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 233 | hzhen线勤丰纺织支线04杆~hzhen线勤丰纺织支线05杆 | hzhen线勤丰纺织支线04杆 | hzhen线勤丰纺织支线05杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 234 | 10kVhzhen线63#杆~10kVhzhen线64#杆 | 10kVhzhen线63#杆 | 10kVhzhen线64#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 235 | 10kVhzhen线65#杆~10kVhzhen线66#杆 | 10kVhzhen线65#杆 | 10kVhzhen线66#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 236 | 10kVhzhen线88杆~10kVhzhen线89杆 | 10kVhzhen线88杆 | 10kVhzhen线89杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 237 | 10kVhzhen线66#杆~10kVhzhen线67#杆 | 10kVhzhen线66#杆 | 10kVhzhen线67#杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 238 | 10kVhzhen线75杆~10kVhzhen线75-01杆 | 10kVhzhen线75杆 | 10kVhzhen线75-01杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 239 | 工业园区支线05杆~工业园区支线06杆 | 工业园区支线05杆 | 工业园区支线06杆 | 60 | JKLYJ/Q-10-240 | 邳州_10kV河镇线明细.xlsx

## 09_节点表_原始
馈线别名 | 中文名 | 馈线编号 | 110kV站 | raw节点名 | 建议canonical节点名 | 原始分量ID | 度 | 叶节点 | 分支节点 | 备注
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线10杆 | dji南台支线10杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线11杆 | dji南台支线11杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线12杆 | dji南台支线12杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线13杆 | dji南台支线13杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线14杆 | dji南台支线14杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线15杆 | dji南台支线15杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线1杆 | dji南台支线1杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线2杆 | dji南台支线2杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线3杆 | dji南台支线3杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线4杆 | dji南台支线4杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线5杆 | dji南台支线5杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线6杆 | dji南台支线6杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线7杆 | dji南台支线7杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线8杆 | dji南台支线8杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dji南台支线9杆 | dji南台支线9杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线01杆 | dnan线01杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线02杆 | dnan线02杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线03杆 | dnan线03杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线04杆 | dnan线04杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线05杆 | dnan线05杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线06杆 | dnan线06杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线07杆 | dnan线07杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线08杆 | dnan线08杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线09杆 | dnan线09杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线10+1 | dnan线10+1 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线100杆 | dnan线100杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线101杆 | dnan线101杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线102杆 | dnan线102杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线103杆 | dnan线103杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线10杆 | dnan线10杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线11杆 | dnan线11杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线12杆 | dnan线12杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线13杆 | dnan线13杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线14杆 | dnan线14杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线15杆 | dnan线15杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线16杆 | dnan线16杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线17杆 | dnan线17杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线18杆 | dnan线18杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线19杆 | dnan线19杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线20杆 | dnan线20杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线21杆 | dnan线21杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线22杆 | dnan线22杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线23杆 | dnan线23杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线24杆 | dnan线24杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线25杆 | dnan线25杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线26杆 | dnan线26杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线27杆 | dnan线27杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线28杆 | dnan线28杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线29杆 | dnan线29杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线30杆 | dnan线30杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线31杆 | dnan线31杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线32杆 | dnan线32杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线33杆 | dnan线33杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线34杆 | dnan线34杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线35杆 | dnan线35杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线36杆 | dnan线36杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线37杆 | dnan线37杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线38杆 | dnan线38杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线39杆 | dnan线39杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线40杆 | dnan线40杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线41杆 | dnan线41杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线42杆 | dnan线42杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线43杆 | dnan线43杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线44杆 | dnan线44杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线45杆 | dnan线45杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线46-1 | dnan线46-1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线46-2 | dnan线46-2 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线46杆 | dnan线46杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线47杆 | dnan线47杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线48杆 | dnan线48杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线49杆 | dnan线49杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线50杆 | dnan线50杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线51杆 | dnan线51杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线52杆 | dnan线52杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-1 | dnan线53-1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-2 | dnan线53-2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-3 | dnan线53-3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-4 | dnan线53-4 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-5 | dnan线53-5 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-6 | dnan线53-6 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53-7 | dnan线53-7 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线53杆 | dnan线53杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线54杆 | dnan线54杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线55杆 | dnan线55杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线56-1 | dnan线56-1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线56-2 | dnan线56-2 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线56杆 | dnan线56杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线57杆 | dnan线57杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线58杆 | dnan线58杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线59杆 | dnan线59杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线60杆 | dnan线60杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线61杆 | dnan线61杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线62杆 | dnan线62杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线63杆 | dnan线63杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线64杆 | dnan线64杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线65杆 | dnan线65杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线66杆 | dnan线66杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线67杆 | dnan线67杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线68杆 | dnan线68杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线69杆 | dnan线69杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线70杆 | dnan线70杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线71杆 | dnan线71杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线72杆 | dnan线72杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-1 | dnan线73-1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-10 | dnan线73-10 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-11 | dnan线73-11 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-2 | dnan线73-2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-3 | dnan线73-3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-4 | dnan线73-4 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-5 | dnan线73-5 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-6 | dnan线73-6 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-7 | dnan线73-7 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-8 | dnan线73-8 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73-9 | dnan线73-9 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线73杆 | dnan线73杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线74杆 | dnan线74杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线75杆 | dnan线75杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线76杆 | dnan线76杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线77杆 | dnan线77杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线78杆 | dnan线78杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线79杆 | dnan线79杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线80杆 | dnan线80杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线81杆 | dnan线81杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线82-1 | dnan线82-1 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线82杆 | dnan线82杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线83杆 | dnan线83杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线84杆 | dnan线84杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线85杆 | dnan线85杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线86杆 | dnan线86杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线87杆 | dnan线87杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线88杆 | dnan线88杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线89杆 | dnan线89杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线90杆 | dnan线90杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线91杆 | dnan线91杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线92杆 | dnan线92杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线93杆 | dnan线93杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线94杆 | dnan线94杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线95杆 | dnan线95杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线96杆 | dnan线96杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线97杆 | dnan线97杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线98杆 | dnan线98杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线99杆 | dnan线99杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线合金厂支线1杆 | dnan线合金厂支线1杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线合金厂支线2杆 | dnan线合金厂支线2杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线合金厂支线3杆 | dnan线合金厂支线3杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线合金厂支线4杆 | dnan线合金厂支线4杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线01杆 | dnan线天齐七支站支线01杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线02杆 | dnan线天齐七支站支线02杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线03杆 | dnan线天齐七支站支线03杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线04杆 | dnan线天齐七支站支线04杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线05杆 | dnan线天齐七支站支线05杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线06杆 | dnan线天齐七支站支线06杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线07杆 | dnan线天齐七支站支线07杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线08杆 | dnan线天齐七支站支线08杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线09杆 | dnan线天齐七支站支线09杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线10 | dnan线天齐七支站支线10 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线11 | dnan线天齐七支站支线11 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线12 | dnan线天齐七支站支线12 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线天齐七支站支线13 | dnan线天齐七支站支线13 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线01杆 | dnan线恒鼎支线01杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线02杆 | dnan线恒鼎支线02杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线03杆 | dnan线恒鼎支线03杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线04杆 | dnan线恒鼎支线04杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线05杆 | dnan线恒鼎支线05杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线06杆 | dnan线恒鼎支线06杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线07杆 | dnan线恒鼎支线07杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线08杆 | dnan线恒鼎支线08杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线09杆 | dnan线恒鼎支线09杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线10杆 | dnan线恒鼎支线10杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线11杆 | dnan线恒鼎支线11杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线12杆 | dnan线恒鼎支线12杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线13杆 | dnan线恒鼎支线13杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线14杆 | dnan线恒鼎支线14杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线15杆 | dnan线恒鼎支线15杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线16杆 | dnan线恒鼎支线16杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线17杆 | dnan线恒鼎支线17杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线18杆 | dnan线恒鼎支线18杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线19杆 | dnan线恒鼎支线19杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线20杆 | dnan线恒鼎支线20杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线21杆 | dnan线恒鼎支线21杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线22杆 | dnan线恒鼎支线22杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线23杆 | dnan线恒鼎支线23杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线24杆 | dnan线恒鼎支线24杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线25杆 | dnan线恒鼎支线25杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线26杆 | dnan线恒鼎支线26杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线27杆 | dnan线恒鼎支线27杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线28杆 | dnan线恒鼎支线28杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线29杆 | dnan线恒鼎支线29杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线30杆 | dnan线恒鼎支线30杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线31杆 | dnan线恒鼎支线31杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线32杆 | dnan线恒鼎支线32杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线33杆 | dnan线恒鼎支线33杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线34杆 | dnan线恒鼎支线34杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆 | dnan线恒鼎支线35杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-1 | dnan线恒鼎支线35杆-1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-2 | dnan线恒鼎支线35杆-2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-3 | dnan线恒鼎支线35杆-3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-4 | dnan线恒鼎支线35杆-4 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-5 | dnan线恒鼎支线35杆-5 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-6 | dnan线恒鼎支线35杆-6 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-7 | dnan线恒鼎支线35杆-7 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-8 | dnan线恒鼎支线35杆-8 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线35杆-9 | dnan线恒鼎支线35杆-9 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线36杆 | dnan线恒鼎支线36杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线37杆 | dnan线恒鼎支线37杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线38杆 | dnan线恒鼎支线38杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线39杆 | dnan线恒鼎支线39杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线40杆 | dnan线恒鼎支线40杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线41杆 | dnan线恒鼎支线41杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线42杆 | dnan线恒鼎支线42杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线43杆 | dnan线恒鼎支线43杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线44杆 | dnan线恒鼎支线44杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线45杆 | dnan线恒鼎支线45杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线46杆 | dnan线恒鼎支线46杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线47杆 | dnan线恒鼎支线47杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线48杆 | dnan线恒鼎支线48杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线恒鼎支线49杆 | dnan线恒鼎支线49杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线01杆 | dnan线黄安七支站支线01杆 | C02 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线02杆 | dnan线黄安七支站支线02杆 | C02 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线03杆 | dnan线黄安七支站支线03杆 | C02 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线04杆 | dnan线黄安七支站支线04杆 | C02 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线05杆 | dnan线黄安七支站支线05杆 | C02 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安七支站支线06杆 | dnan线黄安七支站支线06杆 | C02 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线01杆 | dnan线黄安六支站支线01杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线02杆 | dnan线黄安六支站支线02杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线03杆 | dnan线黄安六支站支线03杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线04杆 | dnan线黄安六支站支线04杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线05杆 | dnan线黄安六支站支线05杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线06杆 | dnan线黄安六支站支线06杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线07杆 | dnan线黄安六支站支线07杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线08杆 | dnan线黄安六支站支线08杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线09杆 | dnan线黄安六支站支线09杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线10 | dnan线黄安六支站支线10 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线11 | dnan线黄安六支站支线11 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线12 | dnan线黄安六支站支线12 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线13 | dnan线黄安六支站支线13 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线14 | dnan线黄安六支站支线14 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线15 | dnan线黄安六支站支线15 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线16 | dnan线黄安六支站支线16 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线17 | dnan线黄安六支站支线17 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线18 | dnan线黄安六支站支线18 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | dnan线黄安六支站支线9-1杆 | dnan线黄安六支站支线9-1杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线1杆 | 军霞器材支线1杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线2 | 军霞器材支线2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线3 | 军霞器材支线3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线4 | 军霞器材支线4 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线5 | 军霞器材支线5 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线6 | 军霞器材支线6 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线7 | 军霞器材支线7 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 军霞器材支线8 | 军霞器材支线8 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 刘一刀支线1 | 刘一刀支线1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 刘一刀支线2 | 刘一刀支线2 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 国成支线1 | 国成支线1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 国成支线2 | 国成支线2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 国成支线3 | 国成支线3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 国成支线4 | 国成支线4 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 国成支线5 | 国成支线5 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 大晶支线1 | 大晶支线1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 大晶支线2 | 大晶支线2 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 大晶支线3 | 大晶支线3 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 大晶支线4 | 大晶支线4 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线1-1杆 | 波士达支线1-1杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线1杆 | 波士达支线1杆 | C01 | 3 | 否 | 是
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线2杆 | 波士达支线2杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线3杆 | 波士达支线3杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线4杆 | 波士达支线4杆 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 波士达支线5杆 | 波士达支线5杆 | C01 | 1 | 是 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 金凤凰1 | 金凤凰1 | C01 | 2 | 否 | 否
dnan | 墩南线 | PZXL-00092 | 墩集变 | 金凤凰2 | 金凤凰2 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线01杆 | dzhen线01杆 | C04 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线02杆 | dzhen线02杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线03杆 | dzhen线03杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线04杆 | dzhen线04杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线05杆 | dzhen线05杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线06杆 | dzhen线06杆 | C04 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线07杆 | dzhen线07杆 | C04 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线08杆 | dzhen线08杆 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线09杆 | dzhen线09杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线10杆 | dzhen线10杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线11杆 | dzhen线11杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线12杆 | dzhen线12杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线13杆 | dzhen线13杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线14杆 | dzhen线14杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线15杆 | dzhen线15杆 | C01 | 4 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线16杆 | dzhen线16杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线17杆 | dzhen线17杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线18杆 | dzhen线18杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线19杆 | dzhen线19杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线20杆 | dzhen线20杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线21杆 | dzhen线21杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线22杆 | dzhen线22杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线23杆 | dzhen线23杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线24杆 | dzhen线24杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线25杆 | dzhen线25杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线26杆 | dzhen线26杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线27杆 | dzhen线27杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线28杆 | dzhen线28杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线29-1 | dzhen线29-1 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线29杆 | dzhen线29杆 | C01 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线30杆 | dzhen线30杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线31杆 | dzhen线31杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线32杆 | dzhen线32杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线33杆 | dzhen线33杆 | C01 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线34杆 | dzhen线34杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线35杆 | dzhen线35杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线36杆 | dzhen线36杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线37杆 | dzhen线37杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线38杆 | dzhen线38杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线39杆 | dzhen线39杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线40杆 | dzhen线40杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线41杆 | dzhen线41杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线42杆 | dzhen线42杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线43杆 | dzhen线43杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线44杆 | dzhen线44杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线45杆 | dzhen线45杆 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线力达支线1杆 | dzhen线力达支线1杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线力达支线2杆 | dzhen线力达支线2杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线力达支线3杆 | dzhen线力达支线3杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线力达支线4杆 | dzhen线力达支线4杆 | C02 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线01杆 | dzhen线北支线01杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线02杆 | dzhen线北支线02杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线03杆 | dzhen线北支线03杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线04杆 | dzhen线北支线04杆 | C04 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线05杆 | dzhen线北支线05杆 | C04 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线10杆 | dzhen线北支线10杆 | C06 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线北支线11杆 | dzhen线北支线11杆 | C06 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线南方永磁支线2杆 | dzhen线南方永磁支线2杆 | C05 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线南方永磁支线3杆 | dzhen线南方永磁支线3杆 | C05 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线南方永磁支线4杆 | dzhen线南方永磁支线4杆 | C05 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线10杆 | dzhen线恒鼎支线10杆 | C03 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线11杆 | dzhen线恒鼎支线11杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线12杆 | dzhen线恒鼎支线12杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线13杆 | dzhen线恒鼎支线13杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线14杆 | dzhen线恒鼎支线14杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线15杆 | dzhen线恒鼎支线15杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线16杆 | dzhen线恒鼎支线16杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线17杆 | dzhen线恒鼎支线17杆 | C03 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线2杆 | dzhen线恒鼎支线2杆 | C03 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线3杆 | dzhen线恒鼎支线3杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线4杆 | dzhen线恒鼎支线4杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线5杆 | dzhen线恒鼎支线5杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线6杆 | dzhen线恒鼎支线6杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线7杆 | dzhen线恒鼎支线7杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线8杆 | dzhen线恒鼎支线8杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线恒鼎支线9杆 | dzhen线恒鼎支线9杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线昊阳支线1杆 | dzhen线昊阳支线1杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线昊阳支线2杆 | dzhen线昊阳支线2杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线昊阳支线3杆 | dzhen线昊阳支线3杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线昊阳支线4杆 | dzhen线昊阳支线4杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线昊阳支线5杆 | dzhen线昊阳支线5杆 | C02 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线10杆 | dzhen线正康支线10杆 | C03 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线1杆 | dzhen线正康支线1杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线2杆 | dzhen线正康支线2杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线3杆 | dzhen线正康支线3杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线4杆 | dzhen线正康支线4杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线5杆 | dzhen线正康支线5杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线6杆 | dzhen线正康支线6杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线7杆 | dzhen线正康支线7杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线8杆 | dzhen线正康支线8杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线正康支线9杆 | dzhen线正康支线9杆 | C03 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线10杆 | dzhen线污水厂支线10杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线11杆 | dzhen线污水厂支线11杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线12杆 | dzhen线污水厂支线12杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线13-1杆 | dzhen线污水厂支线13-1杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线13杆 | dzhen线污水厂支线13杆 | C02 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线14杆 | dzhen线污水厂支线14杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线15杆 | dzhen线污水厂支线15杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线16杆 | dzhen线污水厂支线16杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线17杆 | dzhen线污水厂支线17杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线18杆 | dzhen线污水厂支线18杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线19杆 | dzhen线污水厂支线19杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线1杆 | dzhen线污水厂支线1杆 | C02 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线20杆 | dzhen线污水厂支线20杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线21杆 | dzhen线污水厂支线21杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线22杆 | dzhen线污水厂支线22杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线23杆 | dzhen线污水厂支线23杆 | C02 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线2杆 | dzhen线污水厂支线2杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线3杆 | dzhen线污水厂支线3杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线4杆 | dzhen线污水厂支线4杆 | C02 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线5杆 | dzhen线污水厂支线5杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线6杆 | dzhen线污水厂支线6杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线7杆 | dzhen线污水厂支线7杆 | C02 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线8杆 | dzhen线污水厂支线8杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线污水厂支线9杆 | dzhen线污水厂支线9杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线长运支线01杆 | dzhen线长运支线01杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | dzhen线长运支线02杆 | dzhen线长运支线02杆 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 三仪支线01杆 | 三仪支线01杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 三仪支线02杆 | 三仪支线02杆 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 利峰支线1 | 利峰支线1 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 利峰支线2 | 利峰支线2 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 利峰支线3 | 利峰支线3 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 利峰支线4 | 利峰支线4 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线10杆 | 海天石化支线10杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线11杆 | 海天石化支线11杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线12杆 | 海天石化支线12杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线13杆 | 海天石化支线13杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线14杆 | 海天石化支线14杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线15杆 | 海天石化支线15杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线16杆 | 海天石化支线16杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线17杆 | 海天石化支线17杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线18杆 | 海天石化支线18杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线19杆 | 海天石化支线19杆 | C01 | 3 | 否 | 是
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线1杆 | 海天石化支线1杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线20杆 | 海天石化支线20杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线21杆 | 海天石化支线21杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线22杆 | 海天石化支线22杆 | C01 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线2杆 | 海天石化支线2杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线3杆 | 海天石化支线3杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线4杆 | 海天石化支线4杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线5杆 | 海天石化支线5杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线6杆 | 海天石化支线6杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线7杆 | 海天石化支线7杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线8杆 | 海天石化支线8杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 海天石化支线9杆 | 海天石化支线9杆 | C01 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线10杆 | 王场湖支线10杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线11杆 | 王场湖支线11杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线12杆 | 王场湖支线12杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线13杆 | 王场湖支线13杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线14杆 | 王场湖支线14杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线15杆 | 王场湖支线15杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线16杆 | 王场湖支线16杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线17杆 | 王场湖支线17杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线18杆 | 王场湖支线18杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线19杆 | 王场湖支线19杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线1杆 | 王场湖支线1杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线20杆 | 王场湖支线20杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线21杆 | 王场湖支线21杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线22杆 | 王场湖支线22杆 | C02 | 1 | 是 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线2杆 | 王场湖支线2杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线3杆 | 王场湖支线3杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线4杆 | 王场湖支线4杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线5杆 | 王场湖支线5杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线6杆 | 王场湖支线6杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线7杆 | 王场湖支线7杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线8杆 | 王场湖支线8杆 | C02 | 2 | 否 | 否
dzhen | 墩振线 | PZXL-00099 | 墩集变 | 王场湖支线9杆 | 王场湖支线9杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线10杆 | dxi北支线10杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线11杆 | dxi北支线11杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线12杆 | dxi北支线12杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线13杆 | dxi北支线13杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线14杆 | dxi北支线14杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线15杆 | dxi北支线15杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线16杆 | dxi北支线16杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线17杆 | dxi北支线17杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线18杆 | dxi北支线18杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线19杆 | dxi北支线19杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线1杆 | dxi北支线1杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线20杆 | dxi北支线20杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线21杆 | dxi北支线21杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线22杆 | dxi北支线22杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线23杆 | dxi北支线23杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线24杆 | dxi北支线24杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线25杆 | dxi北支线25杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线26杆 | dxi北支线26杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线27杆 | dxi北支线27杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线28杆 | dxi北支线28杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线29杆 | dxi北支线29杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线2杆 | dxi北支线2杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线30杆 | dxi北支线30杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线31杆 | dxi北支线31杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线32杆 | dxi北支线32杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线33杆 | dxi北支线33杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线34杆 | dxi北支线34杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线35杆 | dxi北支线35杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线36杆 | dxi北支线36杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线37杆 | dxi北支线37杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线38杆 | dxi北支线38杆 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线39杆 | dxi北支线39杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线3杆 | dxi北支线3杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线40杆 | dxi北支线40杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线41杆 | dxi北支线41杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线42杆 | dxi北支线42杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线43杆 | dxi北支线43杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线4杆 | dxi北支线4杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线5杆 | dxi北支线5杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线6杆 | dxi北支线6杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线7杆 | dxi北支线7杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线8杆 | dxi北支线8杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi北支线9杆 | dxi北支线9杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线01杆 | dxi线01杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线02杆 | dxi线02杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线03杆 | dxi线03杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线04杆 | dxi线04杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线05杆 | dxi线05杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线06杆 | dxi线06杆 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线07杆 | dxi线07杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线08杆 | dxi线08杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线09杆 | dxi线09杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线10杆 | dxi线10杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线11杆 | dxi线11杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线12杆 | dxi线12杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线13-1杆 | dxi线13-1杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线13杆 | dxi线13杆 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线14杆 | dxi线14杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线15杆 | dxi线15杆 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线16杆 | dxi线16杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线17杆 | dxi线17杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线18杆 | dxi线18杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线19杆 | dxi线19杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线20杆 | dxi线20杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线21杆 | dxi线21杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线22杆 | dxi线22杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线23杆 | dxi线23杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线24杆 | dxi线24杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线25杆 | dxi线25杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线26杆 | dxi线26杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线27杆 | dxi线27杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线28杆 | dxi线28杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线29杆 | dxi线29杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线30杆 | dxi线30杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线31杆 | dxi线31杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线32杆 | dxi线32杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线33杆 | dxi线33杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线34杆 | dxi线34杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线35杆 | dxi线35杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线36杆 | dxi线36杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线37杆 | dxi线37杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线38杆 | dxi线38杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线39杆 | dxi线39杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线40杆 | dxi线40杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线41杆 | dxi线41杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线42杆 | dxi线42杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线43杆 | dxi线43杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线44-1杆 | dxi线44-1杆 | C02 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线44杆 | dxi线44杆 | C02 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线10杆 | dxi线企服中心支线10杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线11杆 | dxi线企服中心支线11杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线12杆 | dxi线企服中心支线12杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线13杆 | dxi线企服中心支线13杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线14杆 | dxi线企服中心支线14杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线15杆 | dxi线企服中心支线15杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线16杆 | dxi线企服中心支线16杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线17杆 | dxi线企服中心支线17杆 | C02 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线1杆 | dxi线企服中心支线1杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线2杆 | dxi线企服中心支线2杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线3杆 | dxi线企服中心支线3杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线4杆 | dxi线企服中心支线4杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线5杆 | dxi线企服中心支线5杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线6杆 | dxi线企服中心支线6杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线7杆 | dxi线企服中心支线7杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线8杆 | dxi线企服中心支线8杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线企服中心支线9杆 | dxi线企服中心支线9杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线兴春支线01杆 | dxi线兴春支线01杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线兴春支线02杆 | dxi线兴春支线02杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线兴春支线03杆 | dxi线兴春支线03杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线兴春支线04杆 | dxi线兴春支线04杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线北支线38-1杆 | dxi线北支线38-1杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线合金厂支线01杆 | dxi线合金厂支线01杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线合金厂支线02杆 | dxi线合金厂支线02杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线10杆 | dxi线国成支线10杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线1杆 | dxi线国成支线1杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线2杆 | dxi线国成支线2杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线3杆 | dxi线国成支线3杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线4杆 | dxi线国成支线4杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线5杆 | dxi线国成支线5杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线6杆 | dxi线国成支线6杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线7杆 | dxi线国成支线7杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线8杆 | dxi线国成支线8杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线国成支线9杆 | dxi线国成支线9杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线1杆 | dxi线日托支线1杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线2杆 | dxi线日托支线2杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线3杆 | dxi线日托支线3杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线4杆 | dxi线日托支线4杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线5杆 | dxi线日托支线5杆 | C02 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线日托支线6杆 | dxi线日托支线6杆 | C02 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线01 | dxi线海天石化支线01 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线02 | dxi线海天石化支线02 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线03 | dxi线海天石化支线03 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线04 | dxi线海天石化支线04 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线05 | dxi线海天石化支线05 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线06 | dxi线海天石化支线06 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线07 | dxi线海天石化支线07 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线08 | dxi线海天石化支线08 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线09 | dxi线海天石化支线09 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线10 | dxi线海天石化支线10 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线11 | dxi线海天石化支线11 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线12 | dxi线海天石化支线12 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线13 | dxi线海天石化支线13 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线14 | dxi线海天石化支线14 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线15 | dxi线海天石化支线15 | C01 | 4 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线16 | dxi线海天石化支线16 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线17 | dxi线海天石化支线17 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线18 | dxi线海天石化支线18 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线19 | dxi线海天石化支线19 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线20 | dxi线海天石化支线20 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线21 | dxi线海天石化支线21 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线22 | dxi线海天石化支线22 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线23 | dxi线海天石化支线23 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线24 | dxi线海天石化支线24 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线25 | dxi线海天石化支线25 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线26 | dxi线海天石化支线26 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线27 | dxi线海天石化支线27 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线28 | dxi线海天石化支线28 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线29 | dxi线海天石化支线29 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线30 | dxi线海天石化支线30 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线31 | dxi线海天石化支线31 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线32 | dxi线海天石化支线32 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线33 | dxi线海天石化支线33 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线34 | dxi线海天石化支线34 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线35 | dxi线海天石化支线35 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线36 | dxi线海天石化支线36 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线37 | dxi线海天石化支线37 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线38 | dxi线海天石化支线38 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线39 | dxi线海天石化支线39 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线40杆 | dxi线海天石化支线40杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线41杆 | dxi线海天石化支线41杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线42杆 | dxi线海天石化支线42杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线43杆 | dxi线海天石化支线43杆 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线海天石化支线44杆 | dxi线海天石化支线44杆 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线01 | dxi线王场湖支线01 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线02 | dxi线王场湖支线02 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线03 | dxi线王场湖支线03 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线04 | dxi线王场湖支线04 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线05 | dxi线王场湖支线05 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线06 | dxi线王场湖支线06 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线07 | dxi线王场湖支线07 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线08 | dxi线王场湖支线08 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线09 | dxi线王场湖支线09 | C01 | 3 | 否 | 是
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线10 | dxi线王场湖支线10 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线11 | dxi线王场湖支线11 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线12 | dxi线王场湖支线12 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线13 | dxi线王场湖支线13 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线14 | dxi线王场湖支线14 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线7-1 | dxi线王场湖支线7-1 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线7-2 | dxi线王场湖支线7-2 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线7-3 | dxi线王场湖支线7-3 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线7-4 | dxi线王场湖支线7-4 | C01 | 2 | 否 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线王场湖支线7-5 | dxi线王场湖支线7-5 | C01 | 1 | 是 | 否
dxi | 墩西线 | PZXL-00097 | 墩集变 | dxi线高速路变支线01杆 | dxi线高速路变支线01杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 3队电站支01 | 3队电站支01 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong支线01杆 | hdong支线01杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong支线02杆 | hdong支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong支线03杆 | hdong支线03杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线10杆 | hdong线10杆 | C07 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线11杆 | hdong线11杆 | C07 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线12-1 | hdong线12-1 | C04 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线12杆 | hdong线12杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线13杆 | hdong线13杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线14杆 | hdong线14杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线15杆 | hdong线15杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线16杆 | hdong线16杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线17杆 | hdong线17杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线18杆 | hdong线18杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线19杆 | hdong线19杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线1杆 | hdong线1杆 | C05 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线20杆 | hdong线20杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线21杆 | hdong线21杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线22杆 | hdong线22杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线23杆 | hdong线23杆 | C04 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线24杆 | hdong线24杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线25杆 | hdong线25杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线26杆 | hdong线26杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线27杆 | hdong线27杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线28杆 | hdong线28杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线29杆 | hdong线29杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线2杆 | hdong线2杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线30杆 | hdong线30杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线31杆 | hdong线31杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线32杆 | hdong线32杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线33杆 | hdong线33杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线34杆 | hdong线34杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线35杆 | hdong线35杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线36杆 | hdong线36杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线37杆 | hdong线37杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线38杆 | hdong线38杆 | C03 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线39杆 | hdong线39杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线3杆 | hdong线3杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线40杆 | hdong线40杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线41杆 | hdong线41杆 | C03 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线43杆 | hdong线43杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线44杆 | hdong线44杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线45杆 | hdong线45杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线46杆 | hdong线46杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线47杆 | hdong线47杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线49杆 | hdong线49杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线4杆 | hdong线4杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线50杆 | hdong线50杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线51杆 | hdong线51杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线52杆 | hdong线52杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线53杆 | hdong线53杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线54杆 | hdong线54杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线55杆 | hdong线55杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线56-1杆 | hdong线56-1杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线56杆 | hdong线56杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线57杆 | hdong线57杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线58杆 | hdong线58杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线59杆 | hdong线59杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线5杆 | hdong线5杆 | C05 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线60杆 | hdong线60杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线61杆 | hdong线61杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线62杆 | hdong线62杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线63杆 | hdong线63杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线64杆 | hdong线64杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线65杆 | hdong线65杆 | C01 | 4 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线66杆 | hdong线66杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线67杆 | hdong线67杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线68杆 | hdong线68杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线69杆 | hdong线69杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线6杆 | hdong线6杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线70杆 | hdong线70杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线71杆 | hdong线71杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线72杆 | hdong线72杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线73杆 | hdong线73杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74-01杆 | hdong线74-01杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74-02杆 | hdong线74-02杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74-03杆 | hdong线74-03杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74-04杆 | hdong线74-04杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74-05杆 | hdong线74-05杆 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线74杆 | hdong线74杆 | C02 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线75杆 | hdong线75杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线76杆 | hdong线76杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线77杆 | hdong线77杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线78杆 | hdong线78杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线79-1杆 | hdong线79-1杆 | C02 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线79-2杆 | hdong线79-2杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线79-3杆 | hdong线79-3杆 | C02 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线79-4杆 | hdong线79-4杆 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线79杆 | hdong线79杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线7杆 | hdong线7杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线80杆 | hdong线80杆 | C02 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线81杆 | hdong线81杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线82杆 | hdong线82杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线83杆 | hdong线83杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线84杆 | hdong线84杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线85杆 | hdong线85杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线86杆 | hdong线86杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线87杆 | hdong线87杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线88杆 | hdong线88杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线89杆 | hdong线89杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线8杆 | hdong线8杆 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线90杆 | hdong线90杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线91杆 | hdong线91杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线92杆 | hdong线92杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线93杆 | hdong线93杆 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线9杆 | hdong线9杆 | C05 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线01杆 | hdong线张村2#变支线01杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线02杆 | hdong线张村2#变支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线03杆 | hdong线张村2#变支线03杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线04杆 | hdong线张村2#变支线04杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线05杆 | hdong线张村2#变支线05杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线06杆 | hdong线张村2#变支线06杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线07-1杆 | hdong线张村2#变支线07-1杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线07杆 | hdong线张村2#变支线07杆 | C01 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线08杆 | hdong线张村2#变支线08杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线09杆 | hdong线张村2#变支线09杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线10杆 | hdong线张村2#变支线10杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线11杆 | hdong线张村2#变支线11杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线12杆 | hdong线张村2#变支线12杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线13杆 | hdong线张村2#变支线13杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线14杆 | hdong线张村2#变支线14杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线15杆 | hdong线张村2#变支线15杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线16杆 | hdong线张村2#变支线16杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线17杆 | hdong线张村2#变支线17杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线18杆 | hdong线张村2#变支线18杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线张村2#变支线19杆 | hdong线张村2#变支线19杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线01杆 | hdong线汇龙支线01杆 | C04 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线02杆 | hdong线汇龙支线02杆 | C06 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线03杆 | hdong线汇龙支线03杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线04杆 | hdong线汇龙支线04杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线05杆 | hdong线汇龙支线05杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线06杆 | hdong线汇龙支线06杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线07杆 | hdong线汇龙支线07杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线08杆 | hdong线汇龙支线08杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线09杆 | hdong线汇龙支线09杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线10杆 | hdong线汇龙支线10杆 | C06 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | hdong线汇龙支线11杆 | hdong线汇龙支线11杆 | C06 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线01杆 | 勤丰纺织支线01杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线02杆 | 勤丰纺织支线02杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线03杆 | 勤丰纺织支线03杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线04杆 | 勤丰纺织支线04杆 | C02 | 3 | 否 | 是
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线05杆 | 勤丰纺织支线05杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线06杆 | 勤丰纺织支线06杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线07杆 | 勤丰纺织支线07杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线08杆 | 勤丰纺织支线08杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线09杆 | 勤丰纺织支线09杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线10杆 | 勤丰纺织支线10杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线11杆 | 勤丰纺织支线11杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线12杆 | 勤丰纺织支线12杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线13杆 | 勤丰纺织支线13杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 勤丰纺织支线14杆 | 勤丰纺织支线14杆 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 华运蒜业支线01杆 | 华运蒜业支线01杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 华运蒜业支线02杆 | 华运蒜业支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 华运蒜业支线03杆 | 华运蒜业支线03杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 宏达支01 | 宏达支01 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产二支线01杆 | 恒东房地产二支线01杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产二支线02杆 | 恒东房地产二支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产二支线03杆 | 恒东房地产二支线03杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产支线01杆 | 恒东房地产支线01杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产支线02杆 | 恒东房地产支线02杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 恒东房地产支线03杆 | 恒东房地产支线03杆 | C03 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 日松馆业支线01杆 | 日松馆业支线01杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 日松馆业支线02杆 | 日松馆业支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 日松馆业支线03杆 | 日松馆业支线03杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 李口八队电站支线01 | 李口八队电站支线01 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 李口八队电站支线02 | 李口八队电站支线02 | C05 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 李口八队电站支线03 | 李口八队电站支线03 | C05 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线01杆 | 河湾1#支线01杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线02杆 | 河湾1#支线02杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线03杆 | 河湾1#支线03杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线04杆 | 河湾1#支线04杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线05杆 | 河湾1#支线05杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线06杆 | 河湾1#支线06杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线07杆 | 河湾1#支线07杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线08杆 | 河湾1#支线08杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线09杆 | 河湾1#支线09杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线10杆 | 河湾1#支线10杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线11杆 | 河湾1#支线11杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线12杆 | 河湾1#支线12杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线13杆 | 河湾1#支线13杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线14杆 | 河湾1#支线14杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线15杆 | 河湾1#支线15杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线16杆 | 河湾1#支线16杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线17杆 | 河湾1#支线17杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线18杆 | 河湾1#支线18杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线19杆 | 河湾1#支线19杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线20杆 | 河湾1#支线20杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线21杆 | 河湾1#支线21杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线22杆 | 河湾1#支线22杆 | C01 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾1#支线23杆 | 河湾1#支线23杆 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河湾四队电站支01 | 河湾四队电站支01 | C01 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 河镇线hdong42杆 | hdong线42杆 | C01 | 2 | 否 | 否 | 疑似命名串线；建议保留raw并建立canonical映射
hdong | 河东线 | PZXL-00154 | 河湾变 | 河镇线hdong48杆 | hdong线48杆 | C01 | 2 | 否 | 否 | 疑似命名串线；图纸联络点按hdong48识别
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线01杆 | 煤球厂支线01杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线02杆 | 煤球厂支线02杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线03杆 | 煤球厂支线03杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线04杆 | 煤球厂支线04杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线05杆 | 煤球厂支线05杆 | C03 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 煤球厂支线06杆 | 煤球厂支线06杆 | C03 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 环境卫生管理处支线01杆 | 环境卫生管理处支线01杆 | C02 | 1 | 是 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 贝斯卡拉支线001杆 | 贝斯卡拉支线001杆 | C02 | 2 | 否 | 否
hdong | 河东线 | PZXL-00154 | 河湾变 | 贝斯卡拉支线002杆 | 贝斯卡拉支线002杆 | C02 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线01杆 | hpao线01杆 | C01 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线02杆 | hpao线02杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线03杆 | hpao线03杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线04杆 | hpao线04杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线05杆 | hpao线05杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线06杆 | hpao线06杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线07杆 | hpao线07杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线08杆 | hpao线08杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线09杆 | hpao线09杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线10杆 | hpao线10杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线11杆 | hpao线11杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线12杆 | hpao线12杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线13杆 | hpao线13杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线14杆 | hpao线14杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线15杆 | hpao线15杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线16杆 | hpao线16杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线17杆 | hpao线17杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线18杆 | hpao线18杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线19杆 | hpao线19杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线20杆 | hpao线20杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线21杆 | hpao线21杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线22杆 | hpao线22杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线23杆 | hpao线23杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线24杆 | hpao线24杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线25杆 | hpao线25杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线26杆 | hpao线26杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线27杆 | hpao线27杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线28杆 | hpao线28杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线29杆 | hpao线29杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线30杆 | hpao线30杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线31杆 | hpao线31杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线32杆 | hpao线32杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线33杆 | hpao线33杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线34杆 | hpao线34杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线35杆 | hpao线35杆 | C01 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线36杆 | hpao线36杆 | C01 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线37杆 | hpao线37杆 | C04 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线38杆 | hpao线38杆 | C04 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线39杆 | hpao线39杆 | C04 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线40杆 | hpao线40杆 | C04 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线41杆 | hpao线41杆 | C04 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线42杆 | hpao线42杆 | C04 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线43杆 | hpao线43杆 | C05 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线44杆 | hpao线44杆 | C02 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线45杆 | hpao线45杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线46杆 | hpao线46杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线47杆 | hpao线47杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线48杆 | hpao线48杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线49杆 | hpao线49杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线50杆 | hpao线50杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线51杆 | hpao线51杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线52杆 | hpao线52杆 | C02 | 3 | 否 | 是
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线53杆 | hpao线53杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线54杆 | hpao线54杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线55杆 | hpao线55杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线56杆 | hpao线56杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线57杆 | hpao线57杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线58杆 | hpao线58杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线59杆 | hpao线59杆 | C02 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线01杆 | hpao线墩既村高坡塑料颗粒产支线01杆 | C03 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线02杆 | hpao线墩既村高坡塑料颗粒产支线02杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线03杆 | hpao线墩既村高坡塑料颗粒产支线03杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线04杆 | hpao线墩既村高坡塑料颗粒产支线04杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线05杆 | hpao线墩既村高坡塑料颗粒产支线05杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线06杆 | hpao线墩既村高坡塑料颗粒产支线06杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线07杆 | hpao线墩既村高坡塑料颗粒产支线07杆 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线10 | hpao线墩既村高坡塑料颗粒产支线10 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线11 | hpao线墩既村高坡塑料颗粒产支线11 | C03 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线8 | hpao线墩既村高坡塑料颗粒产支线8 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线墩既村高坡塑料颗粒产支线9 | hpao线墩既村高坡塑料颗粒产支线9 | C03 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线王场湖排灌站支线1杆 | hpao线王场湖排灌站支线1杆 | C05 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线王场湖支线1杆 | hpao线王场湖支线1杆 | C06 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线王场湖支线2杆 | hpao线王场湖支线2杆 | C06 | 1 | 是 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线盛川支线1杆 | hpao线盛川支线1杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线盛川支线2杆 | hpao线盛川支线2杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线盛川支线3杆 | hpao线盛川支线3杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线盛川支线4杆 | hpao线盛川支线4杆 | C02 | 2 | 否 | 否
hpao | 河炮线 | PZXL-00161 | 河湾变 | hpao线盛川支线5杆 | hpao线盛川支线5杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线01#杆 | 10kVhzhen线01#杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线02#杆 | 10kVhzhen线02#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线03#杆 | 10kVhzhen线03#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线04#杆 | 10kVhzhen线04#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线05#杆 | 10kVhzhen线05#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线06#杆 | 10kVhzhen线06#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线08#杆 | 10kVhzhen线08#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线09#杆 | 10kVhzhen线09#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线10#杆 | 10kVhzhen线10#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线11#杆 | 10kVhzhen线11#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线12#杆 | 10kVhzhen线12#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线13#杆 | 10kVhzhen线13#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线14#杆 | 10kVhzhen线14#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线15#杆 | 10kVhzhen线15#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线16#杆 | 10kVhzhen线16#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线17#杆 | 10kVhzhen线17#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线18#杆 | 10kVhzhen线18#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线19#杆 | 10kVhzhen线19#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线20#杆 | 10kVhzhen线20#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线21#杆 | 10kVhzhen线21#杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线22#杆 | 10kVhzhen线22#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线23#杆 | 10kVhzhen线23#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线24#杆 | 10kVhzhen线24#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线25#杆 | 10kVhzhen线25#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线26#杆 | 10kVhzhen线26#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线27#杆 | 10kVhzhen线27#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线28#杆 | 10kVhzhen线28#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线29#杆 | 10kVhzhen线29#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线30#杆 | 10kVhzhen线30#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线31#杆 | 10kVhzhen线31#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线32#杆 | 10kVhzhen线32#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线33#杆 | 10kVhzhen线33#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线34#杆 | 10kVhzhen线34#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线35#杆 | 10kVhzhen线35#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线36#杆 | 10kVhzhen线36#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线37#杆 | 10kVhzhen线37#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线38#杆 | 10kVhzhen线38#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线39#杆 | 10kVhzhen线39#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线40#杆 | 10kVhzhen线40#杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线41#杆 | 10kVhzhen线41#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线42#杆 | 10kVhzhen线42#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线43#杆 | 10kVhzhen线43#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线44#杆 | 10kVhzhen线44#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线46#杆 | 10kVhzhen线46#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线47#杆 | 10kVhzhen线47#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线48#杆 | 10kVhzhen线48#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线49#杆 | 10kVhzhen线49#杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线50#杆 | 10kVhzhen线50#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线51#杆 | 10kVhzhen线51#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线52#杆 | 10kVhzhen线52#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线53#杆 | 10kVhzhen线53#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线54#杆 | 10kVhzhen线54#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线55#杆 | 10kVhzhen线55#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线56#杆 | 10kVhzhen线56#杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线57#杆 | 10kVhzhen线57#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线58#杆 | 10kVhzhen线58#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线59#杆 | 10kVhzhen线59#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线60#杆 | 10kVhzhen线60#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线61#杆 | 10kVhzhen线61#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线62#杆 | 10kVhzhen线62#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线63#杆 | 10kVhzhen线63#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线64#杆 | 10kVhzhen线64#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线65#杆 | 10kVhzhen线65#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线66#杆 | 10kVhzhen线66#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线67#杆 | 10kVhzhen线67#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线68#杆 | 10kVhzhen线68#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线69#杆 | 10kVhzhen线69#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线70#杆 | 10kVhzhen线70#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线71#杆 | 10kVhzhen线71#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线72#杆 | 10kVhzhen线72#杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线73#杆 | 10kVhzhen线73#杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线74杆 | 10kVhzhen线74杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75-01杆 | 10kVhzhen线75-01杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75-02杆 | 10kVhzhen线75-02杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75-03杆 | 10kVhzhen线75-03杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75-04杆 | 10kVhzhen线75-04杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75-05杆 | 10kVhzhen线75-05杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线75杆 | 10kVhzhen线75杆 | C02 | 4 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线76杆 | 10kVhzhen线76杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线77杆 | 10kVhzhen线77杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线78杆 | 10kVhzhen线78杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线79杆 | 10kVhzhen线79杆 | C02 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线80杆 | 10kVhzhen线80杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线81杆 | 10kVhzhen线81杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线82杆 | 10kVhzhen线82杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线83杆 | 10kVhzhen线83杆 | C02 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线84杆 | 10kVhzhen线84杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线85杆 | 10kVhzhen线85杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线86杆 | 10kVhzhen线86杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线87杆 | 10kVhzhen线87杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线88杆 | 10kVhzhen线88杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线89杆 | 10kVhzhen线89杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线90杆 | 10kVhzhen线90杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线91杆 | 10kVhzhen线91杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线92杆 | 10kVhzhen线92杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 10kVhzhen线93杆 | 10kVhzhen线93杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线07杆 | hzhen线07杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线45杆 | hzhen线45杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线56-1 | hzhen线56-1 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线01杆 | hzhen线勤丰纺织支线01杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线02杆 | hzhen线勤丰纺织支线02杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线03杆 | hzhen线勤丰纺织支线03杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线04杆 | hzhen线勤丰纺织支线04杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线05杆 | hzhen线勤丰纺织支线05杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线06杆 | hzhen线勤丰纺织支线06杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线07杆 | hzhen线勤丰纺织支线07杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线08杆 | hzhen线勤丰纺织支线08杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | hzhen线勤丰纺织支线09杆 | hzhen线勤丰纺织支线09杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线10杆 | 南方永磁支线10杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线11杆 | 南方永磁支线11杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线12杆 | 南方永磁支线12杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线13杆 | 南方永磁支线13杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线14杆 | 南方永磁支线14杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线15杆 | 南方永磁支线15杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线16杆 | 南方永磁支线16杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线17杆 | 南方永磁支线17杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线18杆 | 南方永磁支线18杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线19杆 | 南方永磁支线19杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线1杆 | 南方永磁支线1杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线2杆 | 南方永磁支线2杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线3杆 | 南方永磁支线3杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线4杆 | 南方永磁支线4杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线5杆 | 南方永磁支线5杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线6杆 | 南方永磁支线6杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线7杆 | 南方永磁支线7杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线8杆 | 南方永磁支线8杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 南方永磁支线9杆 | 南方永磁支线9杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 垃圾站支线01杆 | 垃圾站支线01杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 垃圾站支线02杆 | 垃圾站支线02杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 垃圾站支线03杆 | 垃圾站支线03杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 垃圾站支线04杆 | 垃圾站支线04杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线01杆 | 工业园区支线01杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线02杆 | 工业园区支线02杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线03杆 | 工业园区支线03杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线04杆 | 工业园区支线04杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线05杆 | 工业园区支线05杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线06杆 | 工业园区支线06杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线07杆 | 工业园区支线07杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线08杆 | 工业园区支线08杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线09杆 | 工业园区支线09杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线10杆 | 工业园区支线10杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线11杆 | 工业园区支线11杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线12杆 | 工业园区支线12杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线13杆 | 工业园区支线13杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线14杆 | 工业园区支线14杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线15杆 | 工业园区支线15杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线16杆 | 工业园区支线16杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线17杆 | 工业园区支线17杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 工业园区支线18杆 | 工业园区支线18杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线01杆 | 张村10变支线01杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线02杆 | 张村10变支线02杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线03杆 | 张村10变支线03杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线04杆 | 张村10变支线04杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线05杆 | 张村10变支线05杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线06杆 | 张村10变支线06杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线07杆 | 张村10变支线07杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村10变支线08杆 | 张村10变支线08杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线01杆 | 张村1变支线01杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线02杆 | 张村1变支线02杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线03杆 | 张村1变支线03杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线04杆 | 张村1变支线04杆 | C02 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线05杆 | 张村1变支线05杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线06杆 | 张村1变支线06杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线07杆 | 张村1变支线07杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线08杆 | 张村1变支线08杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线09杆 | 张村1变支线09杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线10杆 | 张村1变支线10杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线11杆 | 张村1变支线11杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线12杆 | 张村1变支线12杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线13杆 | 张村1变支线13杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线14杆 | 张村1变支线14杆 | C02 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线15杆 | 张村1变支线15杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线16杆 | 张村1变支线16杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线17杆 | 张村1变支线17杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线18杆 | 张村1变支线18杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线19杆 | 张村1变支线19杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线20杆 | 张村1变支线20杆 | C02 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线21杆 | 张村1变支线21杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线22杆 | 张村1变支线22杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线23杆 | 张村1变支线23杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线24杆 | 张村1变支线24杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线25杆 | 张村1变支线25杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线26杆 | 张村1变支线26杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线27杆 | 张村1变支线27杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线28杆 | 张村1变支线28杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线29杆 | 张村1变支线29杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线30杆 | 张村1变支线30杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线31杆 | 张村1变支线31杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线32杆 | 张村1变支线32杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线33杆 | 张村1变支线33杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线34杆 | 张村1变支线34杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线35杆 | 张村1变支线35杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线36杆 | 张村1变支线36杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线37杆 | 张村1变支线37杆 | C02 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 张村1变支线38杆 | 张村1变支线38杆 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线10杆 | 文苑路支线10杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线11杆 | 文苑路支线11杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线12杆 | 文苑路支线12杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线13杆 | 文苑路支线13杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线14杆 | 文苑路支线14杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线15杆 | 文苑路支线15杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线16杆 | 文苑路支线16杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线17杆 | 文苑路支线17杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线18杆 | 文苑路支线18杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线19杆 | 文苑路支线19杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线1杆 | 文苑路支线1杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线20杆 | 文苑路支线20杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线21杆 | 文苑路支线21杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线22杆 | 文苑路支线22杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线23杆 | 文苑路支线23杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线24杆 | 文苑路支线24杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线25杆 | 文苑路支线25杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线26杆 | 文苑路支线26杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线27杆 | 文苑路支线27杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线28杆 | 文苑路支线28杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线29杆 | 文苑路支线29杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线2杆 | 文苑路支线2杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线30杆 | 文苑路支线30杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线3杆 | 文苑路支线3杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线4杆 | 文苑路支线4杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线5杆 | 文苑路支线5杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线6杆 | 文苑路支线6杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线7杆 | 文苑路支线7杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线8杆 | 文苑路支线8杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 文苑路支线9杆 | 文苑路支线9杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 欢乐买支线01杆 | 欢乐买支线01杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 欢乐买支线02杆 | 欢乐买支线02杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 欢乐买支线03杆 | 欢乐买支线03杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 河湾4＃变支01 | 河湾4＃变支01 | C02 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线01杆 | 看守所支线01杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线02杆 | 看守所支线02杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线03杆 | 看守所支线03杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线04杆 | 看守所支线04杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线05杆 | 看守所支线05杆 | C01 | 3 | 否 | 是
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线06杆 | 看守所支线06杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线07杆 | 看守所支线07杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线08杆 | 看守所支线08杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线3-01杆 | 看守所支线3-01杆 | C01 | 2 | 否 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 看守所支线3-02杆 | 看守所支线3-02杆 | C01 | 1 | 是 | 否
hzhen | 河镇线 | PZXL-00173 | 河湾变 | 运河张村11变支线01杆 | 运河张村11变支线01杆 | C02 | 1 | 是 | 否

## 10_建模实施顺序
阶段 | 任务 | 输入 | 处理动作 | 输出 | 门槛/状态
S0 | 原始数据固化 | 6份档距段明细 + 6份图纸 | 保留raw节点名/档距段/型号/来源行号，不直接改原始名称 | 08_边表_原始、09_节点表_原始 | 已完成
S1 | 节点标准化 | raw节点表 | 建立canonical节点名；仅对明确错误做映射，保留raw字段 | node_master | 部分完成
S2 | 物理档距图 | raw边表 | 按杆塔-档距段建立physical_span_graph；长度、导线型号作为边属性 | physical_span_graph | 已具备
S3 | 开关设备图 | 图纸 + 开/关状态表 | 抽取开关、分支箱、开闭所、母联，建立switch_graph；不把开关伪造为50m线路 | switch_graph | P0待完成
S4 | 拓扑修复 | 04_拓扑修复清单 | 逐项补齐R001~R021；优先闭环T01/T02/T03相关P0缺口 | repaired_topology | P0待完成
S5 | 运行拓扑生成 | repaired_topology + 常态开合状态 | 按normal_closed生成base operational graph，并检查径向性/孤岛/多电源 | operational_graph_base | P0待完成
S6 | 电气参数化 | 06_导线型号字典 + 开关容量 | 映射R/X/载流量；开关采用设备对象或近零阻抗，不混入线路长度 | branch_parameter_master | P0待完成
S7 | 源荷注入 | 110kV站裕度 + 10kV负荷/PV | 把馈线/配变负荷和PV分配到节点；定义正常峰荷、高PV、N-1工况 | power_injection_cases | P0/P1待完成
S8 | 现有联络评估 | T01→T02→T03 | 逐条求最大可转供能力、瓶颈线路、最低电压、开关操作与失供削减 | tie_transfer_results | 建模阶段
S9 | 站级互济聚合 | 3条跨站通道 + 站内重构 | 避免简单相加；在共同源端/线路约束下联合优化各联络潮流 | CD/可转供能力 | 建模阶段
S10 | 新增联络比较 | GIS候选长度 + 造价 | 在现有联络不足区域提出新建候选，比较增量转供收益与年化成本 | 候选方案集 | P1阶段

## 11_案例场景设计
场景ID | 场景 | 涉及对象 | 操作/计算逻辑 | 核心输出 | 前置条件/说明
C0 | 基准运行拓扑 | 六馈线 | 按已核实常态开合状态运行 | 验证无假孤岛、无非法环网；得到基准潮流/反送 | 所有P0拓扑与参数已闭环
C1 | T01现有跨站联络 | dnan↔hpao | 双向分别考察：墩集→河湾、河湾→墩集；联络闭合并配套分段操作保持径向 | 最大可转供MW、瓶颈、Umin、Imax、开关序列、失供削减 | 优先首个案例；当前结构最完整
C2 | T02现有跨站联络 | dzhen↔hdong | 同C1，重点考察长路径与王场湖支线侧限制 | 同上 | 先完成R005
C3 | T03现有跨站联络 | dxi↔hpao | 同C1，重点考虑hpao王场湖分支箱/分支开关链 | 同上 | 先完成R020
C4 | 三通道联合互济 | T01+T02+T03 | 在共同110kV源端裕度、各馈线热限与电压约束下联合分配转供 | 墩集↔河湾站级最大互济、各通道分配、瓶颈转移 | 不能把3条联络额定能力简单求和
C5 | 河湾站内重构辅助 | T04 hdong↔hzhen | 在C2等跨站转供时测试是否通过同站联络转移局部负荷/释放瓶颈 | 跨站互济增益、额外开关动作 | 二阶段
C6 | 墩集开闭所重构辅助 | T05 dxi↔dzhen | 建立虚拟开闭所节点后，测试站内馈线重构对T02/T03的增益 | 跨站互济增益、径向运行可行性 | 二阶段，先映射开闭所接入点
C7 | N-1对比 | 主变/馈线故障集合 | 比较无联络、现有联络、联合互济、必要时新增联络 | EENS/缺供功率、转供率、约束违背、经济增益 | 与110kV主模型口径统一

## 12_AGENT入口
10kV联络案例｜Agent-ready V5.2（映射关系最终校正版）
映射结论 | 六条馈线→110kV站归属完整，不存在缺口：墩振/墩西/墩南→墩集；河东/河炮/河镇→河湾。
站码 | 墩集=BDZ-00027；河湾=BDZ-00048。
站端边界 | 墩集100MVA（50+50）；河湾150MVA（100+50）；站/主变容量及年度极值已入库。
当前建模层级 | 局部10kV联络采用110kV站级等值源端，因此不要求六条馈线进一步映射到某一段10kV母线/某一台主变。
可选精细化 | 只有未来要把转供结果精确归因到某台主变N-1裕度时，才需要“馈线→母线段→具体主变”；这不是当前数据缺口。
TIE-002 | 已具备拓扑、R/X、有效Imax、馈线P、节点负荷/PV种子、站级边界，可直接进入规划计算。
后续两通道 | TIE-001/TIE-003剩余的是图纸拓扑闭环工作，不是站点映射数据缺失。
真正剩余事项 | 普通分段开关符号校准；TIE-001的R005/R010-R014；TIE-003的R020。均可由现有图纸继续处理。
数据层状态 | 对当前局部10kV站级聚合案例，已无必须继续向甲方补充的关键映射数据。
执行入口 | README_AGENT.md → MODEL_CONFIG.yaml → data/agent_tasks.csv。

## 13_feeder_master
feeder_id | feeder_alias | feeder_name | station_id | station_name | base_kv | source_root_name | source_root_node_id | span_count | node_count_physical | structured_length_km | old_total_length_km | old_overhead_length_km | old_cable_length_km | supply_radius_km | feeder_max_allowed_current_a | max_allowed_mva_at_10kv | 2025_max_current_a | 2025_max_p_raw_mw | 2025_max_loading_pct | current_based_s_mva | implied_pf_if_p_valid | model_boundary_p_mw | model_boundary_p_source | raw_installed_capacity_kva | raw_installed_capacity_quality | transformer_count_raw | status | quality_note
PZXL-00092 | dnan | 墩南线 | BDZ-00027 | 墩集变 | 10 | dnan线01杆 | PZXL-00092-N0016 | 267 | 269 | 13.35 | 13.338 | 13.3 | 0.038 | 5.168 | 485 | 8.4004 | 392.52 | 6.5296 | 80.93 | 6.7986 | 0.9604 | 6.5296 | SRC06_2025_MAX_P | 200 | INVALID_AS_FEEDER_TOTAL | 39 | PREPARED | 年度最大P用于馈线历史应力边界；六馈线最大值不视为同一同步时刻。
PZXL-00099 | dzhen | 墩振线 | BDZ-00027 | 墩集变 | 10 | dzhen线01杆 | PZXL-00099-N0001 | 161 | 167 | 8.05 | 11.8276 | 11.4 | 0.4276 | 2.7176 | 595 | 10.3057 | 507 | 8.2344 | 85.21 | 8.7815 | 0.9377 | 8.2344 | SRC06_2025_MAX_P | 1110 | SUSPECT_INCOMPLETE | 52 | PREPARED | 年度最大P用于馈线历史应力边界；六馈线最大值不视为同一同步时刻。
PZXL-00097 | dxi | 墩西线 | BDZ-00027 | 墩集变 | 10 | dxi线01杆 | PZXL-00097-N0044 | 191 | 193 | 9.55 | 10.0397 | 9.3 | 0.7397 | 3.3647 | 485 | 8.4004 | 208.56 | 3.3938 | 43 | 3.6124 | 0.9395 | 3.3938 | SRC06_2025_MAX_P | 3000 | SUSPECT_INCOMPLETE | 31 | PREPARED | 年度最大P用于馈线历史应力边界；六馈线最大值不视为同一同步时刻。
PZXL-00154 | hdong | 河东线 | BDZ-00048 | 河湾变 | 10 | hdong线1杆 | PZXL-00154-N0016 | 195 | 202 | 9.75 | 11.2939 | 9.75 | 1.5439 | 4.1187 | 600 | 10.3923 | 544.57 | 0 | 90.76 | 9.4322 |  | 8.9606 | DERIVED_FROM_2025_MAX_CURRENT_AT_PF0.95; RAW_P=0_ANOMALY | 28600 | PLAUSIBLE_BUT_UNVERIFIED | 77 | PREPARED | 最大有功=0与544.57A/90.76%负载率冲突；0判为异常缺失，规划边界采用I×PF0.95代理。
PZXL-00161 | hpao | 河炮线 | BDZ-00048 | 河湾变 | 10 | hpao线01杆 | PZXL-00161-N0001 | 72 | 78 | 3.6 | 6.261 | 3.6 | 2.661 | 5.1331 | 595 | 10.3057 | 126.21 | 1.8876 | 21.21 | 2.186 | 0.8635 | 1.8876 | SRC06_2025_MAX_P | 6780 | PLAUSIBLE_BUT_UNVERIFIED | 18 | PREPARED | 年度最大P用于馈线历史应力边界；六馈线最大值不视为同一同步时刻。
PZXL-00173 | hzhen | 河镇线 | BDZ-00048 | 河湾变 | 10 | 10kVhzhen线01#杆 | PZXL-00173-N0001 | 238 | 240 | 13.79 | 14.5876 | 13.74 | 0.8476 | 6.8076 | 605 | 10.4789 | 365.98 | 6.2899 | 60.49 | 6.339 | 0.9923 | 6.2899 | SRC06_2025_MAX_P | 4700 | CONFLICTS_WITH_FIELD_OBS_17225KVA | 38 | PREPARED | 年度最大P用于馈线历史应力边界；六馈线最大值不视为同一同步时刻。

## 14_node_master
node_id | station_id | station_name | feeder_id | feeder_alias | feeder_name | canonical_name | raw_name | original_component_id | degree_raw | is_leaf_raw | is_branch_raw | node_type | is_source | is_tie_endpoint | data_status | notes
PZXL-00092-N0001 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线10杆 | dji南台支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0002 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线11杆 | dji南台支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0003 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线12杆 | dji南台支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0004 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线13杆 | dji南台支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0005 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线14杆 | dji南台支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0006 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线15杆 | dji南台支线15杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0007 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线1杆 | dji南台支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0008 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线2杆 | dji南台支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0009 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线3杆 | dji南台支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0010 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线4杆 | dji南台支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0011 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线5杆 | dji南台支线5杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0012 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线6杆 | dji南台支线6杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0013 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线7杆 | dji南台支线7杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0014 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线8杆 | dji南台支线8杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0015 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dji南台支线9杆 | dji南台支线9杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0016 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线01杆 | dnan线01杆 | C01 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0017 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线02杆 | dnan线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0018 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线03杆 | dnan线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0019 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线04杆 | dnan线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0020 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线05杆 | dnan线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0021 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线06杆 | dnan线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0022 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线07杆 | dnan线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0023 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线08杆 | dnan线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0024 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线09杆 | dnan线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0025 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线10+1 | dnan线10+1 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0026 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线100杆 | dnan线100杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0027 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线101杆 | dnan线101杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0028 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线102杆 | dnan线102杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0029 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线103杆 | dnan线103杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0030 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线10杆 | dnan线10杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0031 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线11杆 | dnan线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0032 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线12杆 | dnan线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0033 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线13杆 | dnan线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0034 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线14杆 | dnan线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0035 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线15杆 | dnan线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0036 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线16杆 | dnan线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0037 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线17杆 | dnan线17杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0038 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线18杆 | dnan线18杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0039 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线19杆 | dnan线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0040 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线20杆 | dnan线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0041 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线21杆 | dnan线21杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0042 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线22杆 | dnan线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0043 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线23杆 | dnan线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0044 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线24杆 | dnan线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0045 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线25杆 | dnan线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0046 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线26杆 | dnan线26杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0047 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线27杆 | dnan线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0048 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线28杆 | dnan线28杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0049 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线29杆 | dnan线29杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0050 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线30杆 | dnan线30杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0051 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线31杆 | dnan线31杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0052 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线32杆 | dnan线32杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0053 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线33杆 | dnan线33杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0054 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线34杆 | dnan线34杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0055 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线35杆 | dnan线35杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0056 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线36杆 | dnan线36杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0057 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线37杆 | dnan线37杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0058 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线38杆 | dnan线38杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0059 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线39杆 | dnan线39杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0060 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线40杆 | dnan线40杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0061 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线41杆 | dnan线41杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0062 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线42杆 | dnan线42杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0063 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线43杆 | dnan线43杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0064 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线44杆 | dnan线44杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0065 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线45杆 | dnan线45杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0066 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线46-1 | dnan线46-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0067 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线46-2 | dnan线46-2 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0068 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线46杆 | dnan线46杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0069 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线47杆 | dnan线47杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0070 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线48杆 | dnan线48杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0071 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线49杆 | dnan线49杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0072 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线50杆 | dnan线50杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0073 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线51杆 | dnan线51杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0074 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线52杆 | dnan线52杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0075 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-1 | dnan线53-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0076 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-2 | dnan线53-2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0077 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-3 | dnan线53-3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0078 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-4 | dnan线53-4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0079 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-5 | dnan线53-5 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0080 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-6 | dnan线53-6 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0081 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53-7 | dnan线53-7 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0082 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线53杆 | dnan线53杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0083 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线54杆 | dnan线54杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0084 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线55杆 | dnan线55杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0085 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线56-1 | dnan线56-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0086 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线56-2 | dnan线56-2 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0087 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线56杆 | dnan线56杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0088 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线57杆 | dnan线57杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0089 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线58杆 | dnan线58杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0090 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线59杆 | dnan线59杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0091 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线60杆 | dnan线60杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0092 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线61杆 | dnan线61杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0093 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线62杆 | dnan线62杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0094 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线63杆 | dnan线63杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0095 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线64杆 | dnan线64杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0096 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线65杆 | dnan线65杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0097 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线66杆 | dnan线66杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0098 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线67杆 | dnan线67杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0099 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线68杆 | dnan线68杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0100 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线69杆 | dnan线69杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0101 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线70杆 | dnan线70杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0102 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线71杆 | dnan线71杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0103 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线72杆 | dnan线72杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0104 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-1 | dnan线73-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0105 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-10 | dnan线73-10 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0106 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-11 | dnan线73-11 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0107 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-2 | dnan线73-2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0108 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-3 | dnan线73-3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0109 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-4 | dnan线73-4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0110 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-5 | dnan线73-5 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0111 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-6 | dnan线73-6 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0112 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-7 | dnan线73-7 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0113 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-8 | dnan线73-8 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0114 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73-9 | dnan线73-9 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0115 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线73杆 | dnan线73杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0116 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线74杆 | dnan线74杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0117 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线75杆 | dnan线75杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0118 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线76杆 | dnan线76杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0119 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线77杆 | dnan线77杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0120 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线78杆 | dnan线78杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0121 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线79杆 | dnan线79杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0122 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线80杆 | dnan线80杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0123 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线81杆 | dnan线81杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0124 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线82-1 | dnan线82-1 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0125 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线82杆 | dnan线82杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0126 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线83杆 | dnan线83杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0127 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线84杆 | dnan线84杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0128 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线85杆 | dnan线85杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0129 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线86杆 | dnan线86杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0130 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线87杆 | dnan线87杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0131 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线88杆 | dnan线88杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0132 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线89杆 | dnan线89杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0133 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线90杆 | dnan线90杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0134 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线91杆 | dnan线91杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0135 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线92杆 | dnan线92杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0136 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线93杆 | dnan线93杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0137 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线94杆 | dnan线94杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0138 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线95杆 | dnan线95杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0139 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线96杆 | dnan线96杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0140 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线97杆 | dnan线97杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0141 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线98杆 | dnan线98杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0142 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线99杆 | dnan线99杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0143 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线合金厂支线1杆 | dnan线合金厂支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0144 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线合金厂支线2杆 | dnan线合金厂支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0145 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线合金厂支线3杆 | dnan线合金厂支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0146 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线合金厂支线4杆 | dnan线合金厂支线4杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0147 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线01杆 | dnan线天齐七支站支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0148 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线02杆 | dnan线天齐七支站支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0149 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线03杆 | dnan线天齐七支站支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0150 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线04杆 | dnan线天齐七支站支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0151 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线05杆 | dnan线天齐七支站支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0152 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线06杆 | dnan线天齐七支站支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0153 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线07杆 | dnan线天齐七支站支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0154 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线08杆 | dnan线天齐七支站支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0155 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线09杆 | dnan线天齐七支站支线09杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0156 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线10 | dnan线天齐七支站支线10 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0157 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线11 | dnan线天齐七支站支线11 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0158 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线12 | dnan线天齐七支站支线12 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0159 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线天齐七支站支线13 | dnan线天齐七支站支线13 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0160 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线01杆 | dnan线恒鼎支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0161 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线02杆 | dnan线恒鼎支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0162 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线03杆 | dnan线恒鼎支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0163 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线04杆 | dnan线恒鼎支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0164 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线05杆 | dnan线恒鼎支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0165 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线06杆 | dnan线恒鼎支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0166 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线07杆 | dnan线恒鼎支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0167 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线08杆 | dnan线恒鼎支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0168 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线09杆 | dnan线恒鼎支线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0169 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线10杆 | dnan线恒鼎支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0170 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线11杆 | dnan线恒鼎支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0171 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线12杆 | dnan线恒鼎支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0172 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线13杆 | dnan线恒鼎支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0173 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线14杆 | dnan线恒鼎支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0174 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线15杆 | dnan线恒鼎支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0175 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线16杆 | dnan线恒鼎支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0176 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线17杆 | dnan线恒鼎支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0177 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线18杆 | dnan线恒鼎支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0178 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线19杆 | dnan线恒鼎支线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0179 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线20杆 | dnan线恒鼎支线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0180 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线21杆 | dnan线恒鼎支线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0181 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线22杆 | dnan线恒鼎支线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0182 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线23杆 | dnan线恒鼎支线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0183 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线24杆 | dnan线恒鼎支线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0184 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线25杆 | dnan线恒鼎支线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0185 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线26杆 | dnan线恒鼎支线26杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0186 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线27杆 | dnan线恒鼎支线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0187 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线28杆 | dnan线恒鼎支线28杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0188 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线29杆 | dnan线恒鼎支线29杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0189 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线30杆 | dnan线恒鼎支线30杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0190 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线31杆 | dnan线恒鼎支线31杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0191 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线32杆 | dnan线恒鼎支线32杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0192 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线33杆 | dnan线恒鼎支线33杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0193 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线34杆 | dnan线恒鼎支线34杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0194 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆 | dnan线恒鼎支线35杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0195 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-1 | dnan线恒鼎支线35杆-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0196 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-2 | dnan线恒鼎支线35杆-2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0197 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-3 | dnan线恒鼎支线35杆-3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0198 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-4 | dnan线恒鼎支线35杆-4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0199 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-5 | dnan线恒鼎支线35杆-5 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0200 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-6 | dnan线恒鼎支线35杆-6 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0201 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-7 | dnan线恒鼎支线35杆-7 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0202 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-8 | dnan线恒鼎支线35杆-8 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0203 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线35杆-9 | dnan线恒鼎支线35杆-9 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0204 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线36杆 | dnan线恒鼎支线36杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0205 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线37杆 | dnan线恒鼎支线37杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0206 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线38杆 | dnan线恒鼎支线38杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0207 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线39杆 | dnan线恒鼎支线39杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0208 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线40杆 | dnan线恒鼎支线40杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0209 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线41杆 | dnan线恒鼎支线41杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0210 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线42杆 | dnan线恒鼎支线42杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0211 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线43杆 | dnan线恒鼎支线43杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0212 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线44杆 | dnan线恒鼎支线44杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0213 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线45杆 | dnan线恒鼎支线45杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0214 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线46杆 | dnan线恒鼎支线46杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0215 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线47杆 | dnan线恒鼎支线47杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0216 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线48杆 | dnan线恒鼎支线48杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0217 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线恒鼎支线49杆 | dnan线恒鼎支线49杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0218 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线01杆 | dnan线黄安七支站支线01杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0219 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线02杆 | dnan线黄安七支站支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0220 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线03杆 | dnan线黄安七支站支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0221 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线04杆 | dnan线黄安七支站支线04杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0222 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线05杆 | dnan线黄安七支站支线05杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0223 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安七支站支线06杆 | dnan线黄安七支站支线06杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0224 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线01杆 | dnan线黄安六支站支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0225 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线02杆 | dnan线黄安六支站支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0226 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线03杆 | dnan线黄安六支站支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0227 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线04杆 | dnan线黄安六支站支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0228 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线05杆 | dnan线黄安六支站支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0229 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线06杆 | dnan线黄安六支站支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0230 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线07杆 | dnan线黄安六支站支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0231 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线08杆 | dnan线黄安六支站支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0232 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线09杆 | dnan线黄安六支站支线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0233 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线10 | dnan线黄安六支站支线10 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0234 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线11 | dnan线黄安六支站支线11 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0235 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线12 | dnan线黄安六支站支线12 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0236 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线13 | dnan线黄安六支站支线13 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0237 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线14 | dnan线黄安六支站支线14 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0238 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线15 | dnan线黄安六支站支线15 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0239 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线16 | dnan线黄安六支站支线16 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0240 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线17 | dnan线黄安六支站支线17 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0241 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线18 | dnan线黄安六支站支线18 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0242 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线黄安六支站支线9-1杆 | dnan线黄安六支站支线9-1杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0243 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线1杆 | 军霞器材支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0244 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线2 | 军霞器材支线2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0245 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线3 | 军霞器材支线3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0246 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线4 | 军霞器材支线4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0247 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线5 | 军霞器材支线5 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0248 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线6 | 军霞器材支线6 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0249 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线7 | 军霞器材支线7 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0250 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 军霞器材支线8 | 军霞器材支线8 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0251 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 刘一刀支线1 | 刘一刀支线1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0252 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 刘一刀支线2 | 刘一刀支线2 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0253 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 国成支线1 | 国成支线1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0254 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 国成支线2 | 国成支线2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0255 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 国成支线3 | 国成支线3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0256 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 国成支线4 | 国成支线4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0257 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 国成支线5 | 国成支线5 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0258 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 大晶支线1 | 大晶支线1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0259 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 大晶支线2 | 大晶支线2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0260 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 大晶支线3 | 大晶支线3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0261 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 大晶支线4 | 大晶支线4 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0262 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线1-1杆 | 波士达支线1-1杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0263 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线1杆 | 波士达支线1杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0264 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线2杆 | 波士达支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0265 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线3杆 | 波士达支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0266 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线4杆 | 波士达支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0267 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 波士达支线5杆 | 波士达支线5杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0268 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 金凤凰1 | 金凤凰1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00092-N0269 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | 金凤凰2 | 金凤凰2 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0001 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线01杆 | dzhen线01杆 | C04 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0002 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线02杆 | dzhen线02杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0003 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线03杆 | dzhen线03杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0004 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线04杆 | dzhen线04杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0005 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线05杆 | dzhen线05杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0006 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线06杆 | dzhen线06杆 | C04 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0007 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线07杆 | dzhen线07杆 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0008 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线08杆 | dzhen线08杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0009 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线09杆 | dzhen线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0010 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线10杆 | dzhen线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0011 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线11杆 | dzhen线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0012 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线12杆 | dzhen线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0013 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线13杆 | dzhen线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0014 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线14杆 | dzhen线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0015 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线15杆 | dzhen线15杆 | C01 | 4 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0016 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线16杆 | dzhen线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0017 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线17杆 | dzhen线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0018 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线18杆 | dzhen线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0019 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线19杆 | dzhen线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0020 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线20杆 | dzhen线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0021 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线21杆 | dzhen线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0022 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线22杆 | dzhen线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0023 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线23杆 | dzhen线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0024 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线24杆 | dzhen线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0025 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线25杆 | dzhen线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0026 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线26杆 | dzhen线26杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0027 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线27杆 | dzhen线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0028 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线28杆 | dzhen线28杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0029 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线29-1 | dzhen线29-1 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0030 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线29杆 | dzhen线29杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0031 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线30杆 | dzhen线30杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0032 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线31杆 | dzhen线31杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0033 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线32杆 | dzhen线32杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0034 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线33杆 | dzhen线33杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0035 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线34杆 | dzhen线34杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0036 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线35杆 | dzhen线35杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0037 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线36杆 | dzhen线36杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0038 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线37杆 | dzhen线37杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0039 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线38杆 | dzhen线38杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0040 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线39杆 | dzhen线39杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0041 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线40杆 | dzhen线40杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0042 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线41杆 | dzhen线41杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0043 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线42杆 | dzhen线42杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0044 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线43杆 | dzhen线43杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0045 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线44杆 | dzhen线44杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0046 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线45杆 | dzhen线45杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0047 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线力达支线1杆 | dzhen线力达支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0048 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线力达支线2杆 | dzhen线力达支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0049 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线力达支线3杆 | dzhen线力达支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0050 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线力达支线4杆 | dzhen线力达支线4杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0051 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线01杆 | dzhen线北支线01杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0052 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线02杆 | dzhen线北支线02杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0053 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线03杆 | dzhen线北支线03杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0054 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线04杆 | dzhen线北支线04杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0055 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线05杆 | dzhen线北支线05杆 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0056 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线10杆 | dzhen线北支线10杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0057 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线北支线11杆 | dzhen线北支线11杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0058 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线南方永磁支线2杆 | dzhen线南方永磁支线2杆 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0059 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线南方永磁支线3杆 | dzhen线南方永磁支线3杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0060 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线南方永磁支线4杆 | dzhen线南方永磁支线4杆 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0061 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线10杆 | dzhen线恒鼎支线10杆 | C03 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0062 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线11杆 | dzhen线恒鼎支线11杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0063 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线12杆 | dzhen线恒鼎支线12杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0064 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线13杆 | dzhen线恒鼎支线13杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0065 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线14杆 | dzhen线恒鼎支线14杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0066 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线15杆 | dzhen线恒鼎支线15杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0067 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线16杆 | dzhen线恒鼎支线16杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0068 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线17杆 | dzhen线恒鼎支线17杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0069 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线2杆 | dzhen线恒鼎支线2杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0070 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线3杆 | dzhen线恒鼎支线3杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0071 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线4杆 | dzhen线恒鼎支线4杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0072 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线5杆 | dzhen线恒鼎支线5杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0073 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线6杆 | dzhen线恒鼎支线6杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0074 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线7杆 | dzhen线恒鼎支线7杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0075 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线8杆 | dzhen线恒鼎支线8杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0076 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线恒鼎支线9杆 | dzhen线恒鼎支线9杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0077 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线昊阳支线1杆 | dzhen线昊阳支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0078 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线昊阳支线2杆 | dzhen线昊阳支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0079 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线昊阳支线3杆 | dzhen线昊阳支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0080 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线昊阳支线4杆 | dzhen线昊阳支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0081 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线昊阳支线5杆 | dzhen线昊阳支线5杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0082 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线10杆 | dzhen线正康支线10杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0083 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线1杆 | dzhen线正康支线1杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0084 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线2杆 | dzhen线正康支线2杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0085 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线3杆 | dzhen线正康支线3杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0086 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线4杆 | dzhen线正康支线4杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0087 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线5杆 | dzhen线正康支线5杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0088 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线6杆 | dzhen线正康支线6杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0089 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线7杆 | dzhen线正康支线7杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0090 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线8杆 | dzhen线正康支线8杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0091 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线正康支线9杆 | dzhen线正康支线9杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0092 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线10杆 | dzhen线污水厂支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0093 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线11杆 | dzhen线污水厂支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0094 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线12杆 | dzhen线污水厂支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0095 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线13-1杆 | dzhen线污水厂支线13-1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0096 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线13杆 | dzhen线污水厂支线13杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0097 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线14杆 | dzhen线污水厂支线14杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0098 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线15杆 | dzhen线污水厂支线15杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0099 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线16杆 | dzhen线污水厂支线16杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0100 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线17杆 | dzhen线污水厂支线17杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0101 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线18杆 | dzhen线污水厂支线18杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0102 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线19杆 | dzhen线污水厂支线19杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0103 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线1杆 | dzhen线污水厂支线1杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0104 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线20杆 | dzhen线污水厂支线20杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0105 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线21杆 | dzhen线污水厂支线21杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0106 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线22杆 | dzhen线污水厂支线22杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0107 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线23杆 | dzhen线污水厂支线23杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0108 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线2杆 | dzhen线污水厂支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0109 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线3杆 | dzhen线污水厂支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0110 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线4杆 | dzhen线污水厂支线4杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0111 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线5杆 | dzhen线污水厂支线5杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0112 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线6杆 | dzhen线污水厂支线6杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0113 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线7杆 | dzhen线污水厂支线7杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0114 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线8杆 | dzhen线污水厂支线8杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0115 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线污水厂支线9杆 | dzhen线污水厂支线9杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0116 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线长运支线01杆 | dzhen线长运支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0117 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线长运支线02杆 | dzhen线长运支线02杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0118 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 三仪支线01杆 | 三仪支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0119 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 三仪支线02杆 | 三仪支线02杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0120 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 利峰支线1 | 利峰支线1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0121 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 利峰支线2 | 利峰支线2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0122 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 利峰支线3 | 利峰支线3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0123 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 利峰支线4 | 利峰支线4 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0124 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线10杆 | 海天石化支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0125 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线11杆 | 海天石化支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0126 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线12杆 | 海天石化支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0127 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线13杆 | 海天石化支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0128 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线14杆 | 海天石化支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0129 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线15杆 | 海天石化支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0130 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线16杆 | 海天石化支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0131 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线17杆 | 海天石化支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0132 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线18杆 | 海天石化支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0133 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线19杆 | 海天石化支线19杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0134 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线1杆 | 海天石化支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0135 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线20杆 | 海天石化支线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0136 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线21杆 | 海天石化支线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0137 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线22杆 | 海天石化支线22杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0138 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线2杆 | 海天石化支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0139 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线3杆 | 海天石化支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0140 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线4杆 | 海天石化支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0141 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线5杆 | 海天石化支线5杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0142 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线6杆 | 海天石化支线6杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0143 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线7杆 | 海天石化支线7杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0144 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线8杆 | 海天石化支线8杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0145 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 海天石化支线9杆 | 海天石化支线9杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0146 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线10杆 | 王场湖支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0147 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线11杆 | 王场湖支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0148 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线12杆 | 王场湖支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0149 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线13杆 | 王场湖支线13杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0150 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线14杆 | 王场湖支线14杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0151 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线15杆 | 王场湖支线15杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0152 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线16杆 | 王场湖支线16杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0153 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线17杆 | 王场湖支线17杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0154 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线18杆 | 王场湖支线18杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0155 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线19杆 | 王场湖支线19杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0156 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线1杆 | 王场湖支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0157 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线20杆 | 王场湖支线20杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0158 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线21杆 | 王场湖支线21杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0159 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线22杆 | 王场湖支线22杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0160 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线2杆 | 王场湖支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0161 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线3杆 | 王场湖支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0162 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线4杆 | 王场湖支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0163 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线5杆 | 王场湖支线5杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0164 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线6杆 | 王场湖支线6杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0165 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线7杆 | 王场湖支线7杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0166 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线8杆 | 王场湖支线8杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00099-N0167 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | 王场湖支线9杆 | 王场湖支线9杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0001 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线10杆 | dxi北支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0002 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线11杆 | dxi北支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0003 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线12杆 | dxi北支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0004 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线13杆 | dxi北支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0005 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线14杆 | dxi北支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0006 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线15杆 | dxi北支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0007 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线16杆 | dxi北支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0008 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线17杆 | dxi北支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0009 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线18杆 | dxi北支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0010 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线19杆 | dxi北支线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0011 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线1杆 | dxi北支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0012 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线20杆 | dxi北支线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0013 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线21杆 | dxi北支线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0014 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线22杆 | dxi北支线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0015 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线23杆 | dxi北支线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0016 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线24杆 | dxi北支线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0017 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线25杆 | dxi北支线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0018 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线26杆 | dxi北支线26杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0019 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线27杆 | dxi北支线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0020 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线28杆 | dxi北支线28杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0021 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线29杆 | dxi北支线29杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0022 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线2杆 | dxi北支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0023 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线30杆 | dxi北支线30杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0024 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线31杆 | dxi北支线31杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0025 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线32杆 | dxi北支线32杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0026 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线33杆 | dxi北支线33杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0027 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线34杆 | dxi北支线34杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0028 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线35杆 | dxi北支线35杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0029 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线36杆 | dxi北支线36杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0030 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线37杆 | dxi北支线37杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0031 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线38杆 | dxi北支线38杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0032 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线39杆 | dxi北支线39杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0033 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线3杆 | dxi北支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0034 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线40杆 | dxi北支线40杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0035 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线41杆 | dxi北支线41杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0036 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线42杆 | dxi北支线42杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0037 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线43杆 | dxi北支线43杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0038 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线4杆 | dxi北支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0039 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线5杆 | dxi北支线5杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0040 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线6杆 | dxi北支线6杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0041 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线7杆 | dxi北支线7杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0042 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线8杆 | dxi北支线8杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0043 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi北支线9杆 | dxi北支线9杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0044 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线01杆 | dxi线01杆 | C01 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0045 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线02杆 | dxi线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0046 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线03杆 | dxi线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0047 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线04杆 | dxi线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0048 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线05杆 | dxi线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0049 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线06杆 | dxi线06杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0050 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线07杆 | dxi线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0051 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线08杆 | dxi线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0052 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线09杆 | dxi线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0053 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线10杆 | dxi线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0054 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线11杆 | dxi线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0055 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线12杆 | dxi线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0056 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线13-1杆 | dxi线13-1杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0057 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线13杆 | dxi线13杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0058 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线14杆 | dxi线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0059 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线15杆 | dxi线15杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0060 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线16杆 | dxi线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0061 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线17杆 | dxi线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0062 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线18杆 | dxi线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0063 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线19杆 | dxi线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0064 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线20杆 | dxi线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0065 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线21杆 | dxi线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0066 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线22杆 | dxi线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0067 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线23杆 | dxi线23杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0068 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线24杆 | dxi线24杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0069 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线25杆 | dxi线25杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0070 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线26杆 | dxi线26杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0071 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线27杆 | dxi线27杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0072 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线28杆 | dxi线28杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0073 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线29杆 | dxi线29杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0074 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线30杆 | dxi线30杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0075 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线31杆 | dxi线31杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0076 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线32杆 | dxi线32杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0077 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线33杆 | dxi线33杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0078 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线34杆 | dxi线34杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0079 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线35杆 | dxi线35杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0080 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线36杆 | dxi线36杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0081 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线37杆 | dxi线37杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0082 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线38杆 | dxi线38杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0083 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线39杆 | dxi线39杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0084 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线40杆 | dxi线40杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0085 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线41杆 | dxi线41杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0086 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线42杆 | dxi线42杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0087 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线43杆 | dxi线43杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0088 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线44-1杆 | dxi线44-1杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0089 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线44杆 | dxi线44杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0090 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线10杆 | dxi线企服中心支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0091 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线11杆 | dxi线企服中心支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0092 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线12杆 | dxi线企服中心支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0093 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线13杆 | dxi线企服中心支线13杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0094 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线14杆 | dxi线企服中心支线14杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0095 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线15杆 | dxi线企服中心支线15杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0096 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线16杆 | dxi线企服中心支线16杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0097 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线17杆 | dxi线企服中心支线17杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0098 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线1杆 | dxi线企服中心支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0099 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线2杆 | dxi线企服中心支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0100 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线3杆 | dxi线企服中心支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0101 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线4杆 | dxi线企服中心支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0102 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线5杆 | dxi线企服中心支线5杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0103 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线6杆 | dxi线企服中心支线6杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0104 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线7杆 | dxi线企服中心支线7杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0105 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线8杆 | dxi线企服中心支线8杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0106 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线企服中心支线9杆 | dxi线企服中心支线9杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0107 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线兴春支线01杆 | dxi线兴春支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0108 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线兴春支线02杆 | dxi线兴春支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0109 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线兴春支线03杆 | dxi线兴春支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0110 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线兴春支线04杆 | dxi线兴春支线04杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0111 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线北支线38-1杆 | dxi线北支线38-1杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0112 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线合金厂支线01杆 | dxi线合金厂支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0113 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线合金厂支线02杆 | dxi线合金厂支线02杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0114 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线10杆 | dxi线国成支线10杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0115 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线1杆 | dxi线国成支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0116 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线2杆 | dxi线国成支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0117 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线3杆 | dxi线国成支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0118 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线4杆 | dxi线国成支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0119 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线5杆 | dxi线国成支线5杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0120 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线6杆 | dxi线国成支线6杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0121 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线7杆 | dxi线国成支线7杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0122 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线8杆 | dxi线国成支线8杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0123 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线国成支线9杆 | dxi线国成支线9杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0124 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线1杆 | dxi线日托支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0125 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线2杆 | dxi线日托支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0126 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线3杆 | dxi线日托支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0127 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线4杆 | dxi线日托支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0128 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线5杆 | dxi线日托支线5杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0129 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线日托支线6杆 | dxi线日托支线6杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0130 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线01 | dxi线海天石化支线01 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0131 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线02 | dxi线海天石化支线02 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0132 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线03 | dxi线海天石化支线03 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0133 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线04 | dxi线海天石化支线04 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0134 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线05 | dxi线海天石化支线05 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0135 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线06 | dxi线海天石化支线06 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0136 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线07 | dxi线海天石化支线07 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0137 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线08 | dxi线海天石化支线08 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0138 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线09 | dxi线海天石化支线09 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0139 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线10 | dxi线海天石化支线10 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0140 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线11 | dxi线海天石化支线11 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0141 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线12 | dxi线海天石化支线12 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0142 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线13 | dxi线海天石化支线13 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0143 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线14 | dxi线海天石化支线14 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0144 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线15 | dxi线海天石化支线15 | C01 | 4 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0145 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线16 | dxi线海天石化支线16 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0146 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线17 | dxi线海天石化支线17 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0147 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线18 | dxi线海天石化支线18 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0148 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线19 | dxi线海天石化支线19 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0149 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线20 | dxi线海天石化支线20 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0150 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线21 | dxi线海天石化支线21 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0151 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线22 | dxi线海天石化支线22 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0152 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线23 | dxi线海天石化支线23 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0153 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线24 | dxi线海天石化支线24 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0154 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线25 | dxi线海天石化支线25 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0155 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线26 | dxi线海天石化支线26 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0156 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线27 | dxi线海天石化支线27 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0157 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线28 | dxi线海天石化支线28 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0158 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线29 | dxi线海天石化支线29 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0159 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线30 | dxi线海天石化支线30 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0160 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线31 | dxi线海天石化支线31 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0161 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线32 | dxi线海天石化支线32 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0162 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线33 | dxi线海天石化支线33 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0163 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线34 | dxi线海天石化支线34 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0164 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线35 | dxi线海天石化支线35 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0165 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线36 | dxi线海天石化支线36 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0166 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线37 | dxi线海天石化支线37 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0167 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线38 | dxi线海天石化支线38 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0168 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线39 | dxi线海天石化支线39 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0169 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线40杆 | dxi线海天石化支线40杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0170 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线41杆 | dxi线海天石化支线41杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0171 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线42杆 | dxi线海天石化支线42杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0172 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线43杆 | dxi线海天石化支线43杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0173 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线海天石化支线44杆 | dxi线海天石化支线44杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0174 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线01 | dxi线王场湖支线01 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0175 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线02 | dxi线王场湖支线02 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0176 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线03 | dxi线王场湖支线03 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0177 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线04 | dxi线王场湖支线04 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0178 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线05 | dxi线王场湖支线05 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0179 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线06 | dxi线王场湖支线06 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0180 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线07 | dxi线王场湖支线07 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0181 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线08 | dxi线王场湖支线08 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0182 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线09 | dxi线王场湖支线09 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0183 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线10 | dxi线王场湖支线10 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0184 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线11 | dxi线王场湖支线11 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0185 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线12 | dxi线王场湖支线12 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0186 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线13 | dxi线王场湖支线13 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0187 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线14 | dxi线王场湖支线14 | C01 | 1 | 是 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0188 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线7-1 | dxi线王场湖支线7-1 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0189 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线7-2 | dxi线王场湖支线7-2 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0190 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线7-3 | dxi线王场湖支线7-3 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0191 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线7-4 | dxi线王场湖支线7-4 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0192 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线王场湖支线7-5 | dxi线王场湖支线7-5 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00097-N0193 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线高速路变支线01杆 | dxi线高速路变支线01杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0001 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 3队电站支01 | 3队电站支01 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0002 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong支线01杆 | hdong支线01杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0003 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong支线02杆 | hdong支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0004 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong支线03杆 | hdong支线03杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0005 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线10杆 | hdong线10杆 | C07 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0006 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线11杆 | hdong线11杆 | C07 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0007 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线12-1 | hdong线12-1 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0008 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线12杆 | hdong线12杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0009 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线13杆 | hdong线13杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0010 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线14杆 | hdong线14杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0011 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线15杆 | hdong线15杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0012 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线16杆 | hdong线16杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0013 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线17杆 | hdong线17杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0014 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线18杆 | hdong线18杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0015 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线19杆 | hdong线19杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0016 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线1杆 | hdong线1杆 | C05 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0017 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线20杆 | hdong线20杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0018 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线21杆 | hdong线21杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0019 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线22杆 | hdong线22杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0020 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线23杆 | hdong线23杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0021 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线24杆 | hdong线24杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0022 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线25杆 | hdong线25杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0023 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线26杆 | hdong线26杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0024 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线27杆 | hdong线27杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0025 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线28杆 | hdong线28杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0026 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线29杆 | hdong线29杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0027 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线2杆 | hdong线2杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0028 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线30杆 | hdong线30杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0029 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线31杆 | hdong线31杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0030 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线32杆 | hdong线32杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0031 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线33杆 | hdong线33杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0032 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线34杆 | hdong线34杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0033 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线35杆 | hdong线35杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0034 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线36杆 | hdong线36杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0035 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线37杆 | hdong线37杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0036 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线38杆 | hdong线38杆 | C03 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0037 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线39杆 | hdong线39杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0038 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线3杆 | hdong线3杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0039 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线40杆 | hdong线40杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0040 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线41杆 | hdong线41杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0041 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线43杆 | hdong线43杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0042 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线44杆 | hdong线44杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0043 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线45杆 | hdong线45杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0044 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线46杆 | hdong线46杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0045 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线47杆 | hdong线47杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0046 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线49杆 | hdong线49杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0047 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线4杆 | hdong线4杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0048 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线50杆 | hdong线50杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0049 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线51杆 | hdong线51杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0050 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线52杆 | hdong线52杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0051 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线53杆 | hdong线53杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0052 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线54杆 | hdong线54杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0053 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线55杆 | hdong线55杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0054 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线56-1杆 | hdong线56-1杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0055 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线56杆 | hdong线56杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0056 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线57杆 | hdong线57杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0057 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线58杆 | hdong线58杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0058 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线59杆 | hdong线59杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0059 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线5杆 | hdong线5杆 | C05 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0060 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线60杆 | hdong线60杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0061 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线61杆 | hdong线61杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0062 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线62杆 | hdong线62杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0063 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线63杆 | hdong线63杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0064 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线64杆 | hdong线64杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0065 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线65杆 | hdong线65杆 | C01 | 4 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0066 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线66杆 | hdong线66杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0067 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线67杆 | hdong线67杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0068 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线68杆 | hdong线68杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0069 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线69杆 | hdong线69杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0070 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线6杆 | hdong线6杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0071 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线70杆 | hdong线70杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0072 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线71杆 | hdong线71杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0073 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线72杆 | hdong线72杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0074 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线73杆 | hdong线73杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0075 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74-01杆 | hdong线74-01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0076 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74-02杆 | hdong线74-02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0077 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74-03杆 | hdong线74-03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0078 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74-04杆 | hdong线74-04杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0079 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74-05杆 | hdong线74-05杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0080 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线74杆 | hdong线74杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0081 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线75杆 | hdong线75杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0082 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线76杆 | hdong线76杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0083 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线77杆 | hdong线77杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0084 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线78杆 | hdong线78杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0085 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线79-1杆 | hdong线79-1杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0086 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线79-2杆 | hdong线79-2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0087 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线79-3杆 | hdong线79-3杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0088 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线79-4杆 | hdong线79-4杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0089 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线79杆 | hdong线79杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0090 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线7杆 | hdong线7杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0091 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线80杆 | hdong线80杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0092 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线81杆 | hdong线81杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0093 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线82杆 | hdong线82杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0094 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线83杆 | hdong线83杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0095 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线84杆 | hdong线84杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0096 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线85杆 | hdong线85杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0097 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线86杆 | hdong线86杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0098 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线87杆 | hdong线87杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0099 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线88杆 | hdong线88杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0100 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线89杆 | hdong线89杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0101 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线8杆 | hdong线8杆 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0102 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线90杆 | hdong线90杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0103 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线91杆 | hdong线91杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0104 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线92杆 | hdong线92杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0105 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线93杆 | hdong线93杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0106 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线9杆 | hdong线9杆 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0107 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线01杆 | hdong线张村2#变支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0108 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线02杆 | hdong线张村2#变支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0109 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线03杆 | hdong线张村2#变支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0110 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线04杆 | hdong线张村2#变支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0111 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线05杆 | hdong线张村2#变支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0112 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线06杆 | hdong线张村2#变支线06杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0113 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线07-1杆 | hdong线张村2#变支线07-1杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0114 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线07杆 | hdong线张村2#变支线07杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0115 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线08杆 | hdong线张村2#变支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0116 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线09杆 | hdong线张村2#变支线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0117 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线10杆 | hdong线张村2#变支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0118 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线11杆 | hdong线张村2#变支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0119 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线12杆 | hdong线张村2#变支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0120 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线13杆 | hdong线张村2#变支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0121 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线14杆 | hdong线张村2#变支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0122 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线15杆 | hdong线张村2#变支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0123 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线16杆 | hdong线张村2#变支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0124 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线17杆 | hdong线张村2#变支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0125 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线18杆 | hdong线张村2#变支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0126 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线张村2#变支线19杆 | hdong线张村2#变支线19杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0127 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线01杆 | hdong线汇龙支线01杆 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0128 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线02杆 | hdong线汇龙支线02杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0129 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线03杆 | hdong线汇龙支线03杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0130 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线04杆 | hdong线汇龙支线04杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0131 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线05杆 | hdong线汇龙支线05杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0132 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线06杆 | hdong线汇龙支线06杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0133 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线07杆 | hdong线汇龙支线07杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0134 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线08杆 | hdong线汇龙支线08杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0135 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线09杆 | hdong线汇龙支线09杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0136 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线10杆 | hdong线汇龙支线10杆 | C06 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0137 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线汇龙支线11杆 | hdong线汇龙支线11杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0138 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线01杆 | 勤丰纺织支线01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0139 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线02杆 | 勤丰纺织支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0140 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线03杆 | 勤丰纺织支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0141 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线04杆 | 勤丰纺织支线04杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0142 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线05杆 | 勤丰纺织支线05杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0143 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线06杆 | 勤丰纺织支线06杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0144 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线07杆 | 勤丰纺织支线07杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0145 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线08杆 | 勤丰纺织支线08杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0146 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线09杆 | 勤丰纺织支线09杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0147 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线10杆 | 勤丰纺织支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0148 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线11杆 | 勤丰纺织支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0149 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线12杆 | 勤丰纺织支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0150 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线13杆 | 勤丰纺织支线13杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0151 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 勤丰纺织支线14杆 | 勤丰纺织支线14杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0152 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 华运蒜业支线01杆 | 华运蒜业支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0153 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 华运蒜业支线02杆 | 华运蒜业支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0154 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 华运蒜业支线03杆 | 华运蒜业支线03杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0155 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 宏达支01 | 宏达支01 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0156 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产二支线01杆 | 恒东房地产二支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0157 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产二支线02杆 | 恒东房地产二支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0158 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产二支线03杆 | 恒东房地产二支线03杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0159 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产支线01杆 | 恒东房地产支线01杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0160 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产支线02杆 | 恒东房地产支线02杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0161 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 恒东房地产支线03杆 | 恒东房地产支线03杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0162 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 日松馆业支线01杆 | 日松馆业支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0163 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 日松馆业支线02杆 | 日松馆业支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0164 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 日松馆业支线03杆 | 日松馆业支线03杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0165 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 李口八队电站支线01 | 李口八队电站支线01 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0166 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 李口八队电站支线02 | 李口八队电站支线02 | C05 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0167 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 李口八队电站支线03 | 李口八队电站支线03 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0168 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线01杆 | 河湾1#支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0169 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线02杆 | 河湾1#支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0170 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线03杆 | 河湾1#支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0171 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线04杆 | 河湾1#支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0172 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线05杆 | 河湾1#支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0173 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线06杆 | 河湾1#支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0174 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线07杆 | 河湾1#支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0175 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线08杆 | 河湾1#支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0176 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线09杆 | 河湾1#支线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0177 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线10杆 | 河湾1#支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0178 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线11杆 | 河湾1#支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0179 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线12杆 | 河湾1#支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0180 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线13杆 | 河湾1#支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0181 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线14杆 | 河湾1#支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0182 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线15杆 | 河湾1#支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0183 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线16杆 | 河湾1#支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0184 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线17杆 | 河湾1#支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0185 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线18杆 | 河湾1#支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0186 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线19杆 | 河湾1#支线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0187 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线20杆 | 河湾1#支线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0188 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线21杆 | 河湾1#支线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0189 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线22杆 | 河湾1#支线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0190 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾1#支线23杆 | 河湾1#支线23杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0191 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 河湾四队电站支01 | 河湾四队电站支01 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0192 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线42杆 | 河镇线hdong42杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE | 疑似命名串线；建议保留raw并建立canonical映射
PZXL-00154-N0193 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线48杆 | 河镇线hdong48杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE | 疑似命名串线；图纸联络点按hdong48识别
PZXL-00154-N0194 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线01杆 | 煤球厂支线01杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0195 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线02杆 | 煤球厂支线02杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0196 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线03杆 | 煤球厂支线03杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0197 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线04杆 | 煤球厂支线04杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0198 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线05杆 | 煤球厂支线05杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0199 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 煤球厂支线06杆 | 煤球厂支线06杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0200 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 环境卫生管理处支线01杆 | 环境卫生管理处支线01杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0201 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 贝斯卡拉支线001杆 | 贝斯卡拉支线001杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00154-N0202 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | 贝斯卡拉支线002杆 | 贝斯卡拉支线002杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0001 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线01杆 | hpao线01杆 | C01 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0002 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线02杆 | hpao线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0003 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线03杆 | hpao线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0004 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线04杆 | hpao线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0005 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线05杆 | hpao线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0006 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线06杆 | hpao线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0007 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线07杆 | hpao线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0008 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线08杆 | hpao线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0009 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线09杆 | hpao线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0010 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线10杆 | hpao线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0011 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线11杆 | hpao线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0012 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线12杆 | hpao线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0013 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线13杆 | hpao线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0014 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线14杆 | hpao线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0015 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线15杆 | hpao线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0016 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线16杆 | hpao线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0017 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线17杆 | hpao线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0018 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线18杆 | hpao线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0019 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线19杆 | hpao线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0020 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线20杆 | hpao线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0021 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线21杆 | hpao线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0022 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线22杆 | hpao线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0023 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线23杆 | hpao线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0024 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线24杆 | hpao线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0025 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线25杆 | hpao线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0026 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线26杆 | hpao线26杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0027 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线27杆 | hpao线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0028 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线28杆 | hpao线28杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0029 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线29杆 | hpao线29杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0030 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线30杆 | hpao线30杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0031 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线31杆 | hpao线31杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0032 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线32杆 | hpao线32杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0033 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线33杆 | hpao线33杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0034 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线34杆 | hpao线34杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0035 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线35杆 | hpao线35杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0036 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线36杆 | hpao线36杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0037 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线37杆 | hpao线37杆 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0038 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线38杆 | hpao线38杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0039 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线39杆 | hpao线39杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0040 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线40杆 | hpao线40杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0041 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线41杆 | hpao线41杆 | C04 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0042 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线42杆 | hpao线42杆 | C04 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0043 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线43杆 | hpao线43杆 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0044 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线44杆 | hpao线44杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0045 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线45杆 | hpao线45杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0046 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线46杆 | hpao线46杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0047 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线47杆 | hpao线47杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0048 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线48杆 | hpao线48杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0049 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线49杆 | hpao线49杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0050 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线50杆 | hpao线50杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0051 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线51杆 | hpao线51杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0052 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线52杆 | hpao线52杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0053 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线53杆 | hpao线53杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0054 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线54杆 | hpao线54杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0055 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线55杆 | hpao线55杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0056 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线56杆 | hpao线56杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0057 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线57杆 | hpao线57杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0058 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线58杆 | hpao线58杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0059 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线59杆 | hpao线59杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0060 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线01杆 | hpao线墩既村高坡塑料颗粒产支线01杆 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0061 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线02杆 | hpao线墩既村高坡塑料颗粒产支线02杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0062 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线03杆 | hpao线墩既村高坡塑料颗粒产支线03杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0063 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线04杆 | hpao线墩既村高坡塑料颗粒产支线04杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0064 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线05杆 | hpao线墩既村高坡塑料颗粒产支线05杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0065 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线06杆 | hpao线墩既村高坡塑料颗粒产支线06杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0066 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线07杆 | hpao线墩既村高坡塑料颗粒产支线07杆 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0067 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线10 | hpao线墩既村高坡塑料颗粒产支线10 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0068 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线11 | hpao线墩既村高坡塑料颗粒产支线11 | C03 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0069 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线8 | hpao线墩既村高坡塑料颗粒产支线8 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0070 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线墩既村高坡塑料颗粒产支线9 | hpao线墩既村高坡塑料颗粒产支线9 | C03 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0071 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线王场湖排灌站支线1杆 | hpao线王场湖排灌站支线1杆 | C05 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0072 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线王场湖支线1杆 | hpao线王场湖支线1杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0073 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线王场湖支线2杆 | hpao线王场湖支线2杆 | C06 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0074 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线盛川支线1杆 | hpao线盛川支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0075 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线盛川支线2杆 | hpao线盛川支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0076 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线盛川支线3杆 | hpao线盛川支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0077 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线盛川支线4杆 | hpao线盛川支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-N0078 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线盛川支线5杆 | hpao线盛川支线5杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0001 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线01#杆 | 10kVhzhen线01#杆 | C01 | 1 | 是 | 否 | SOURCE_PHYSICAL | True | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0002 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线02#杆 | 10kVhzhen线02#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0003 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线03#杆 | 10kVhzhen线03#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0004 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线04#杆 | 10kVhzhen线04#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0005 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线05#杆 | 10kVhzhen线05#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0006 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线06#杆 | 10kVhzhen线06#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0007 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线08#杆 | 10kVhzhen线08#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0008 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线09#杆 | 10kVhzhen线09#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0009 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线10#杆 | 10kVhzhen线10#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0010 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线11#杆 | 10kVhzhen线11#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0011 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线12#杆 | 10kVhzhen线12#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0012 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线13#杆 | 10kVhzhen线13#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0013 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线14#杆 | 10kVhzhen线14#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0014 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线15#杆 | 10kVhzhen线15#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0015 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线16#杆 | 10kVhzhen线16#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0016 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线17#杆 | 10kVhzhen线17#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0017 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线18#杆 | 10kVhzhen线18#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0018 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线19#杆 | 10kVhzhen线19#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0019 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线20#杆 | 10kVhzhen线20#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0020 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线21#杆 | 10kVhzhen线21#杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0021 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线22#杆 | 10kVhzhen线22#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0022 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线23#杆 | 10kVhzhen线23#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0023 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线24#杆 | 10kVhzhen线24#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0024 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线25#杆 | 10kVhzhen线25#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0025 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线26#杆 | 10kVhzhen线26#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0026 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线27#杆 | 10kVhzhen线27#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0027 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线28#杆 | 10kVhzhen线28#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0028 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线29#杆 | 10kVhzhen线29#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0029 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线30#杆 | 10kVhzhen线30#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0030 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线31#杆 | 10kVhzhen线31#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0031 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线32#杆 | 10kVhzhen线32#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0032 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线33#杆 | 10kVhzhen线33#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0033 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线34#杆 | 10kVhzhen线34#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0034 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线35#杆 | 10kVhzhen线35#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0035 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线36#杆 | 10kVhzhen线36#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0036 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线37#杆 | 10kVhzhen线37#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0037 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线38#杆 | 10kVhzhen线38#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0038 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线39#杆 | 10kVhzhen线39#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0039 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线40#杆 | 10kVhzhen线40#杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0040 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线41#杆 | 10kVhzhen线41#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0041 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线42#杆 | 10kVhzhen线42#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0042 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线43#杆 | 10kVhzhen线43#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0043 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线44#杆 | 10kVhzhen线44#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0044 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线46#杆 | 10kVhzhen线46#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0045 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线47#杆 | 10kVhzhen线47#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0046 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线48#杆 | 10kVhzhen线48#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0047 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线49#杆 | 10kVhzhen线49#杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | True | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0048 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线50#杆 | 10kVhzhen线50#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0049 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线51#杆 | 10kVhzhen线51#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0050 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线52#杆 | 10kVhzhen线52#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0051 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线53#杆 | 10kVhzhen线53#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0052 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线54#杆 | 10kVhzhen线54#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0053 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线55#杆 | 10kVhzhen线55#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0054 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线56#杆 | 10kVhzhen线56#杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0055 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线57#杆 | 10kVhzhen线57#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0056 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线58#杆 | 10kVhzhen线58#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0057 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线59#杆 | 10kVhzhen线59#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0058 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线60#杆 | 10kVhzhen线60#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0059 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线61#杆 | 10kVhzhen线61#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0060 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线62#杆 | 10kVhzhen线62#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0061 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线63#杆 | 10kVhzhen线63#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0062 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线64#杆 | 10kVhzhen线64#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0063 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线65#杆 | 10kVhzhen线65#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0064 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线66#杆 | 10kVhzhen线66#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0065 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线67#杆 | 10kVhzhen线67#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0066 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线68#杆 | 10kVhzhen线68#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0067 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线69#杆 | 10kVhzhen线69#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0068 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线70#杆 | 10kVhzhen线70#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0069 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线71#杆 | 10kVhzhen线71#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0070 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线72#杆 | 10kVhzhen线72#杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0071 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线73#杆 | 10kVhzhen线73#杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0072 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线74杆 | 10kVhzhen线74杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0073 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75-01杆 | 10kVhzhen线75-01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0074 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75-02杆 | 10kVhzhen线75-02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0075 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75-03杆 | 10kVhzhen线75-03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0076 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75-04杆 | 10kVhzhen线75-04杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0077 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75-05杆 | 10kVhzhen线75-05杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0078 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线75杆 | 10kVhzhen线75杆 | C02 | 4 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0079 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线76杆 | 10kVhzhen线76杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0080 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线77杆 | 10kVhzhen线77杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0081 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线78杆 | 10kVhzhen线78杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0082 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线79杆 | 10kVhzhen线79杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0083 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线80杆 | 10kVhzhen线80杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0084 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线81杆 | 10kVhzhen线81杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0085 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线82杆 | 10kVhzhen线82杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0086 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线83杆 | 10kVhzhen线83杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0087 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线84杆 | 10kVhzhen线84杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0088 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线85杆 | 10kVhzhen线85杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0089 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线86杆 | 10kVhzhen线86杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0090 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线87杆 | 10kVhzhen线87杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0091 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线88杆 | 10kVhzhen线88杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0092 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线89杆 | 10kVhzhen线89杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0093 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线90杆 | 10kVhzhen线90杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0094 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线91杆 | 10kVhzhen线91杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0095 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线92杆 | 10kVhzhen线92杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0096 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线93杆 | 10kVhzhen线93杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0097 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线07杆 | hzhen线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0098 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线45杆 | hzhen线45杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0099 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线56-1 | hzhen线56-1 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0100 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线01杆 | hzhen线勤丰纺织支线01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0101 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线02杆 | hzhen线勤丰纺织支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0102 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线03杆 | hzhen线勤丰纺织支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0103 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线04杆 | hzhen线勤丰纺织支线04杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0104 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线05杆 | hzhen线勤丰纺织支线05杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0105 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线06杆 | hzhen线勤丰纺织支线06杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0106 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线07杆 | hzhen线勤丰纺织支线07杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0107 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线08杆 | hzhen线勤丰纺织支线08杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0108 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | hzhen线勤丰纺织支线09杆 | hzhen线勤丰纺织支线09杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0109 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线10杆 | 南方永磁支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0110 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线11杆 | 南方永磁支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0111 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线12杆 | 南方永磁支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0112 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线13杆 | 南方永磁支线13杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0113 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线14杆 | 南方永磁支线14杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0114 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线15杆 | 南方永磁支线15杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0115 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线16杆 | 南方永磁支线16杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0116 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线17杆 | 南方永磁支线17杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0117 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线18杆 | 南方永磁支线18杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0118 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线19杆 | 南方永磁支线19杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0119 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线1杆 | 南方永磁支线1杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0120 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线2杆 | 南方永磁支线2杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0121 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线3杆 | 南方永磁支线3杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0122 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线4杆 | 南方永磁支线4杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0123 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线5杆 | 南方永磁支线5杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0124 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线6杆 | 南方永磁支线6杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0125 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线7杆 | 南方永磁支线7杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0126 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线8杆 | 南方永磁支线8杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0127 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 南方永磁支线9杆 | 南方永磁支线9杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0128 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 垃圾站支线01杆 | 垃圾站支线01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0129 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 垃圾站支线02杆 | 垃圾站支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0130 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 垃圾站支线03杆 | 垃圾站支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0131 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 垃圾站支线04杆 | 垃圾站支线04杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0132 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线01杆 | 工业园区支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0133 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线02杆 | 工业园区支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0134 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线03杆 | 工业园区支线03杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0135 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线04杆 | 工业园区支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0136 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线05杆 | 工业园区支线05杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0137 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线06杆 | 工业园区支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0138 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线07杆 | 工业园区支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0139 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线08杆 | 工业园区支线08杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0140 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线09杆 | 工业园区支线09杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0141 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线10杆 | 工业园区支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0142 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线11杆 | 工业园区支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0143 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线12杆 | 工业园区支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0144 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线13杆 | 工业园区支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0145 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线14杆 | 工业园区支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0146 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线15杆 | 工业园区支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0147 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线16杆 | 工业园区支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0148 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线17杆 | 工业园区支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0149 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 工业园区支线18杆 | 工业园区支线18杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0150 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线01杆 | 张村10变支线01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0151 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线02杆 | 张村10变支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0152 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线03杆 | 张村10变支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0153 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线04杆 | 张村10变支线04杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0154 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线05杆 | 张村10变支线05杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0155 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线06杆 | 张村10变支线06杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0156 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线07杆 | 张村10变支线07杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0157 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村10变支线08杆 | 张村10变支线08杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0158 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线01杆 | 张村1变支线01杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0159 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线02杆 | 张村1变支线02杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0160 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线03杆 | 张村1变支线03杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0161 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线04杆 | 张村1变支线04杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0162 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线05杆 | 张村1变支线05杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0163 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线06杆 | 张村1变支线06杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0164 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线07杆 | 张村1变支线07杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0165 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线08杆 | 张村1变支线08杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0166 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线09杆 | 张村1变支线09杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0167 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线10杆 | 张村1变支线10杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0168 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线11杆 | 张村1变支线11杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0169 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线12杆 | 张村1变支线12杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0170 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线13杆 | 张村1变支线13杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0171 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线14杆 | 张村1变支线14杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0172 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线15杆 | 张村1变支线15杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0173 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线16杆 | 张村1变支线16杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0174 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线17杆 | 张村1变支线17杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0175 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线18杆 | 张村1变支线18杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0176 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线19杆 | 张村1变支线19杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0177 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线20杆 | 张村1变支线20杆 | C02 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0178 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线21杆 | 张村1变支线21杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0179 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线22杆 | 张村1变支线22杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0180 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线23杆 | 张村1变支线23杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0181 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线24杆 | 张村1变支线24杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0182 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线25杆 | 张村1变支线25杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0183 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线26杆 | 张村1变支线26杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0184 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线27杆 | 张村1变支线27杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0185 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线28杆 | 张村1变支线28杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0186 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线29杆 | 张村1变支线29杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0187 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线30杆 | 张村1变支线30杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0188 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线31杆 | 张村1变支线31杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0189 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线32杆 | 张村1变支线32杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0190 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线33杆 | 张村1变支线33杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0191 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线34杆 | 张村1变支线34杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0192 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线35杆 | 张村1变支线35杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0193 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线36杆 | 张村1变支线36杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0194 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线37杆 | 张村1变支线37杆 | C02 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0195 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 张村1变支线38杆 | 张村1变支线38杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0196 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线10杆 | 文苑路支线10杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0197 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线11杆 | 文苑路支线11杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0198 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线12杆 | 文苑路支线12杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0199 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线13杆 | 文苑路支线13杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0200 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线14杆 | 文苑路支线14杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0201 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线15杆 | 文苑路支线15杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0202 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线16杆 | 文苑路支线16杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0203 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线17杆 | 文苑路支线17杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0204 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线18杆 | 文苑路支线18杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0205 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线19杆 | 文苑路支线19杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0206 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线1杆 | 文苑路支线1杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0207 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线20杆 | 文苑路支线20杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0208 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线21杆 | 文苑路支线21杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0209 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线22杆 | 文苑路支线22杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0210 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线23杆 | 文苑路支线23杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0211 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线24杆 | 文苑路支线24杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0212 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线25杆 | 文苑路支线25杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0213 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线26杆 | 文苑路支线26杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0214 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线27杆 | 文苑路支线27杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0215 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线28杆 | 文苑路支线28杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0216 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线29杆 | 文苑路支线29杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0217 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线2杆 | 文苑路支线2杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0218 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线30杆 | 文苑路支线30杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0219 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线3杆 | 文苑路支线3杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0220 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线4杆 | 文苑路支线4杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0221 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线5杆 | 文苑路支线5杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0222 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线6杆 | 文苑路支线6杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0223 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线7杆 | 文苑路支线7杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0224 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线8杆 | 文苑路支线8杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0225 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 文苑路支线9杆 | 文苑路支线9杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0226 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 欢乐买支线01杆 | 欢乐买支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0227 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 欢乐买支线02杆 | 欢乐买支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0228 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 欢乐买支线03杆 | 欢乐买支线03杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0229 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 河湾4＃变支01 | 河湾4＃变支01 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0230 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线01杆 | 看守所支线01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0231 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线02杆 | 看守所支线02杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0232 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线03杆 | 看守所支线03杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0233 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线04杆 | 看守所支线04杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0234 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线05杆 | 看守所支线05杆 | C01 | 3 | 否 | 是 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0235 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线06杆 | 看守所支线06杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0236 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线07杆 | 看守所支线07杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0237 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线08杆 | 看守所支线08杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0238 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线3-01杆 | 看守所支线3-01杆 | C01 | 2 | 否 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0239 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 看守所支线3-02杆 | 看守所支线3-02杆 | C01 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00173-N0240 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 运河张村11变支线01杆 | 运河张村11变支线01杆 | C02 | 1 | 是 | 否 | PHYSICAL | False | False | CONFIRMED_FROM_STRUCTURED_TABLE
PZXL-00161-V001 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | VIRTUAL::hpao线2分支箱 | hpao线2分支箱 |  |  |  |  | VIRTUAL_DEVICE | False | False | CONFIRMED_DEVICE_FROM_DRAWING_POSITION_APPROX | R020；设备链位置按图纸约束，零长度拓扑节点，不代表新增线路长度
PZXL-00161-V002 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | VIRTUAL::hpao线王场湖支线1分支开关 | hpao线王场湖支线1分支开关（三遥） |  |  |  |  | VIRTUAL_SWITCH | False | False | CONFIRMED_DEVICE_FROM_DRAWING_POSITION_APPROX | R020；三遥分支开关；常态分合状态仍需核实

## 15_physical_edges
edge_id | edge_type | station_id | station_name | feeder_id | feeder_alias | feeder_name | from_node_id | from_node_raw | to_node_id | to_node_raw | length_m | conductor_model | normalized_model | parameter_grade | r_per_km_used | x_per_km_used | r_ohm | x_ohm | ampacity_base_a | ampacity_upper_ref_a | thermal_base_mva_at_10kv | normal_state | source_row | source_file | data_status | feeder_operating_limit_a | effective_rate_a_base | effective_rate_mva_10kv | effective_limit_rule
PZXL-00092-B0001 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0030 | dnan线10杆 | PZXL-00092-N0025 | dnan线10+1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 2 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0002 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0038 | dnan线18杆 | PZXL-00092-N0039 | dnan线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 3 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0003 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0061 | dnan线41杆 | PZXL-00092-N0062 | dnan线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 4 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0004 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0263 | 波士达支线1杆 | PZXL-00092-N0262 | 波士达支线1-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 5 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0005 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0091 | dnan线60杆 | PZXL-00092-N0092 | dnan线61杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 6 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0006 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0263 | 波士达支线1杆 | PZXL-00092-N0264 | 波士达支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 7 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0007 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0060 | dnan线40杆 | PZXL-00092-N0061 | dnan线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 8 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0008 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0030 | dnan线10杆 | PZXL-00092-N0031 | dnan线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 9 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0009 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0034 | dnan线14杆 | PZXL-00092-N0035 | dnan线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 10 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0010 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0224 | dnan线黄安六支站支线01杆 | PZXL-00092-N0225 | dnan线黄安六支站支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 11 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0011 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0251 | 刘一刀支线1 | PZXL-00092-N0252 | 刘一刀支线2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 12 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0012 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0135 | dnan线92杆 | PZXL-00092-N0136 | dnan线93杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 13 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0013 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0232 | dnan线黄安六支站支线09杆 | PZXL-00092-N0242 | dnan线黄安六支站支线9-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 14 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0014 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0138 | dnan线95杆 | PZXL-00092-N0139 | dnan线96杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 15 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0015 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0143 | dnan线合金厂支线1杆 | PZXL-00092-N0144 | dnan线合金厂支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 16 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0016 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0068 | dnan线46杆 | PZXL-00092-N0069 | dnan线47杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 17 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0017 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0069 | dnan线47杆 | PZXL-00092-N0070 | dnan线48杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 18 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0018 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0062 | dnan线42杆 | PZXL-00092-N0143 | dnan线合金厂支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 19 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0019 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0083 | dnan线54杆 | PZXL-00092-N0084 | dnan线55杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 20 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0020 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0063 | dnan线43杆 | PZXL-00092-N0064 | dnan线44杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 21 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0021 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0073 | dnan线51杆 | PZXL-00092-N0074 | dnan线52杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 22 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0022 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0082 | dnan线53杆 | PZXL-00092-N0083 | dnan线54杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 23 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0023 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0072 | dnan线50杆 | PZXL-00092-N0073 | dnan线51杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 24 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0024 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0064 | dnan线44杆 | PZXL-00092-N0065 | dnan线45杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 25 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0025 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0070 | dnan线48杆 | PZXL-00092-N0071 | dnan线49杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 26 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0026 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0071 | dnan线49杆 | PZXL-00092-N0072 | dnan线50杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 27 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0027 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0065 | dnan线45杆 | PZXL-00092-N0068 | dnan线46杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 28 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0028 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0084 | dnan线55杆 | PZXL-00092-N0087 | dnan线56杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 29 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0029 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0062 | dnan线42杆 | PZXL-00092-N0063 | dnan线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 30 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0030 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0074 | dnan线52杆 | PZXL-00092-N0082 | dnan线53杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 31 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0031 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0023 | dnan线08杆 | PZXL-00092-N0024 | dnan线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 32 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0032 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0184 | dnan线恒鼎支线25杆 | PZXL-00092-N0185 | dnan线恒鼎支线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 33 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0033 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0038 | dnan线18杆 | PZXL-00092-N0160 | dnan线恒鼎支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 34 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0034 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0216 | dnan线恒鼎支线48杆 | PZXL-00092-N0217 | dnan线恒鼎支线49杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 35 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0035 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0016 | dnan线01杆 | PZXL-00092-N0017 | dnan线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 36 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0036 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0055 | dnan线35杆 | PZXL-00092-N0056 | dnan线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 37 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0037 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0048 | dnan线28杆 | PZXL-00092-N0049 | dnan线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 38 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0038 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0141 | dnan线98杆 | PZXL-00092-N0142 | dnan线99杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 39 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0039 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0093 | dnan线62杆 | PZXL-00092-N0094 | dnan线63杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 40 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0040 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0043 | dnan线23杆 | PZXL-00092-N0044 | dnan线24杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 41 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0041 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0035 | dnan线15杆 | PZXL-00092-N0036 | dnan线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 42 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0042 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0139 | dnan线96杆 | PZXL-00092-N0140 | dnan线97杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 43 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0043 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0219 | dnan线黄安七支站支线02杆 | PZXL-00092-N0220 | dnan线黄安七支站支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 44 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0044 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0222 | dnan线黄安七支站支线05杆 | PZXL-00092-N0223 | dnan线黄安七支站支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 45 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0045 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0234 | dnan线黄安六支站支线11 | PZXL-00092-N0235 | dnan线黄安六支站支线12 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 46 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0046 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0148 | dnan线天齐七支站支线02杆 | PZXL-00092-N0149 | dnan线天齐七支站支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 47 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0047 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0033 | dnan线13杆 | PZXL-00092-N0034 | dnan线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 48 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0048 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0024 | dnan线09杆 | PZXL-00092-N0030 | dnan线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 49 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0049 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0136 | dnan线93杆 | PZXL-00092-N0137 | dnan线94杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 50 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0050 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0153 | dnan线天齐七支站支线07杆 | PZXL-00092-N0154 | dnan线天齐七支站支线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 51 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0051 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0001 | dji南台支线10杆 | PZXL-00092-N0002 | dji南台支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 52 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0052 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0140 | dnan线97杆 | PZXL-00092-N0141 | dnan线98杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 53 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0053 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0015 | dji南台支线9杆 | PZXL-00092-N0001 | dji南台支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 54 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0054 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0133 | dnan线90杆 | PZXL-00092-N0147 | dnan线天齐七支站支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 55 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0055 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0005 | dji南台支线14杆 | PZXL-00092-N0006 | dji南台支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 56 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0056 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0032 | dnan线12杆 | PZXL-00092-N0033 | dnan线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 57 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0057 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0037 | dnan线17杆 | PZXL-00092-N0038 | dnan线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 58 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0058 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0228 | dnan线黄安六支站支线05杆 | PZXL-00092-N0229 | dnan线黄安六支站支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 59 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0059 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0039 | dnan线19杆 | PZXL-00092-N0040 | dnan线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 60 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0060 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0040 | dnan线20杆 | PZXL-00092-N0041 | dnan线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 61 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0061 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0220 | dnan线黄安七支站支线03杆 | PZXL-00092-N0221 | dnan线黄安七支站支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 62 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0062 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0229 | dnan线黄安六支站支线06杆 | PZXL-00092-N0230 | dnan线黄安六支站支线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 63 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0063 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0003 | dji南台支线12杆 | PZXL-00092-N0004 | dji南台支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 64 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0064 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0042 | dnan线22杆 | PZXL-00092-N0043 | dnan线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 65 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0065 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0137 | dnan线94杆 | PZXL-00092-N0138 | dnan线95杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 66 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0066 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0151 | dnan线天齐七支站支线05杆 | PZXL-00092-N0152 | dnan线天齐七支站支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 67 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0067 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0152 | dnan线天齐七支站支线06杆 | PZXL-00092-N0153 | dnan线天齐七支站支线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 68 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0068 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0154 | dnan线天齐七支站支线08杆 | PZXL-00092-N0155 | dnan线天齐七支站支线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 69 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0069 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0227 | dnan线黄安六支站支线04杆 | PZXL-00092-N0228 | dnan线黄安六支站支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 70 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0070 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0036 | dnan线16杆 | PZXL-00092-N0037 | dnan线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 71 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0071 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0226 | dnan线黄安六支站支线03杆 | PZXL-00092-N0227 | dnan线黄安六支站支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 72 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0072 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0235 | dnan线黄安六支站支线12 | PZXL-00092-N0236 | dnan线黄安六支站支线13 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 73 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0073 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0037 | dnan线17杆 | PZXL-00092-N0243 | 军霞器材支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 74 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0074 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0031 | dnan线11杆 | PZXL-00092-N0032 | dnan线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 75 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0075 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0231 | dnan线黄安六支站支线08杆 | PZXL-00092-N0232 | dnan线黄安六支站支线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 76 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0076 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0134 | dnan线91杆 | PZXL-00092-N0135 | dnan线92杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 77 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0077 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0230 | dnan线黄安六支站支线07杆 | PZXL-00092-N0231 | dnan线黄安六支站支线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 78 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0078 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0218 | dnan线黄安七支站支线01杆 | PZXL-00092-N0219 | dnan线黄安七支站支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 79 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0079 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0002 | dji南台支线11杆 | PZXL-00092-N0003 | dji南台支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 80 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0080 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0221 | dnan线黄安七支站支线04杆 | PZXL-00092-N0222 | dnan线黄安七支站支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 81 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0081 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0048 | dnan线28杆 | PZXL-00092-N0224 | dnan线黄安六支站支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 82 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0082 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0242 | dnan线黄安六支站支线9-1杆 | PZXL-00092-N0233 | dnan线黄安六支站支线10 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 83 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0083 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0133 | dnan线90杆 | PZXL-00092-N0134 | dnan线91杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 84 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0084 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0150 | dnan线天齐七支站支线04杆 | PZXL-00092-N0151 | dnan线天齐七支站支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 85 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0085 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0041 | dnan线21杆 | PZXL-00092-N0042 | dnan线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 86 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0086 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0147 | dnan线天齐七支站支线01杆 | PZXL-00092-N0148 | dnan线天齐七支站支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 87 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0087 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0149 | dnan线天齐七支站支线03杆 | PZXL-00092-N0150 | dnan线天齐七支站支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 88 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0088 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0004 | dji南台支线13杆 | PZXL-00092-N0005 | dji南台支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 89 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0089 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0225 | dnan线黄安六支站支线02杆 | PZXL-00092-N0226 | dnan线黄安六支站支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 90 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0090 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0210 | dnan线恒鼎支线42杆 | PZXL-00092-N0211 | dnan线恒鼎支线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 91 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0091 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0177 | dnan线恒鼎支线18杆 | PZXL-00092-N0178 | dnan线恒鼎支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 92 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0092 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0182 | dnan线恒鼎支线23杆 | PZXL-00092-N0183 | dnan线恒鼎支线24杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 93 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0093 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0049 | dnan线29杆 | PZXL-00092-N0050 | dnan线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 94 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0094 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0183 | dnan线恒鼎支线24杆 | PZXL-00092-N0184 | dnan线恒鼎支线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 95 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0095 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0209 | dnan线恒鼎支线41杆 | PZXL-00092-N0210 | dnan线恒鼎支线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 96 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0096 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0087 | dnan线56杆 | PZXL-00092-N0088 | dnan线57杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 97 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0097 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0022 | dnan线07杆 | PZXL-00092-N0023 | dnan线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 98 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0098 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0094 | dnan线63杆 | PZXL-00092-N0095 | dnan线64杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 99 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0099 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0213 | dnan线恒鼎支线45杆 | PZXL-00092-N0214 | dnan线恒鼎支线46杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 100 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0100 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0176 | dnan线恒鼎支线17杆 | PZXL-00092-N0177 | dnan线恒鼎支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 101 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0101 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0101 | dnan线70杆 | PZXL-00092-N0102 | dnan线71杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 102 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0102 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0090 | dnan线59杆 | PZXL-00092-N0091 | dnan线60杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 103 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0103 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0179 | dnan线恒鼎支线20杆 | PZXL-00092-N0180 | dnan线恒鼎支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 104 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0104 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0054 | dnan线34杆 | PZXL-00092-N0055 | dnan线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 105 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0105 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0027 | dnan线101杆 | PZXL-00092-N0028 | dnan线102杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 106 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0106 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0052 | dnan线32杆 | PZXL-00092-N0053 | dnan线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 107 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0107 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0164 | dnan线恒鼎支线05杆 | PZXL-00092-N0165 | dnan线恒鼎支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 108 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0108 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0167 | dnan线恒鼎支线08杆 | PZXL-00092-N0168 | dnan线恒鼎支线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 109 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0109 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0028 | dnan线102杆 | PZXL-00092-N0029 | dnan线103杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 110 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0110 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0057 | dnan线37杆 | PZXL-00092-N0058 | dnan线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 111 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0111 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0174 | dnan线恒鼎支线15杆 | PZXL-00092-N0175 | dnan线恒鼎支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 112 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0112 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0088 | dnan线57杆 | PZXL-00092-N0089 | dnan线58杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 113 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0113 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0119 | dnan线77杆 | PZXL-00092-N0120 | dnan线78杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 114 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0114 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0050 | dnan线30杆 | PZXL-00092-N0051 | dnan线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 115 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0115 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0122 | dnan线80杆 | PZXL-00092-N0123 | dnan线81杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 116 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0116 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0185 | dnan线恒鼎支线26杆 | PZXL-00092-N0186 | dnan线恒鼎支线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 117 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0117 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0130 | dnan线87杆 | PZXL-00092-N0131 | dnan线88杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 118 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0118 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0165 | dnan线恒鼎支线06杆 | PZXL-00092-N0166 | dnan线恒鼎支线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 119 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0119 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0207 | dnan线恒鼎支线39杆 | PZXL-00092-N0208 | dnan线恒鼎支线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 120 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0120 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0126 | dnan线83杆 | PZXL-00092-N0127 | dnan线84杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 121 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0121 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0187 | dnan线恒鼎支线28杆 | PZXL-00092-N0188 | dnan线恒鼎支线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 122 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0122 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0095 | dnan线64杆 | PZXL-00092-N0096 | dnan线65杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 123 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0123 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0058 | dnan线38杆 | PZXL-00092-N0059 | dnan线39杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 124 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0124 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0020 | dnan线05杆 | PZXL-00092-N0021 | dnan线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 125 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0125 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0056 | dnan线36杆 | PZXL-00092-N0057 | dnan线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 126 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0126 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0116 | dnan线74杆 | PZXL-00092-N0117 | dnan线75杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 127 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0127 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0046 | dnan线26杆 | PZXL-00092-N0047 | dnan线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 128 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0128 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0102 | dnan线71杆 | PZXL-00092-N0103 | dnan线72杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 129 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0129 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0021 | dnan线06杆 | PZXL-00092-N0022 | dnan线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 130 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0130 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0211 | dnan线恒鼎支线43杆 | PZXL-00092-N0212 | dnan线恒鼎支线44杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 131 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0131 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0103 | dnan线72杆 | PZXL-00092-N0115 | dnan线73杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 132 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0132 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0092 | dnan线61杆 | PZXL-00092-N0093 | dnan线62杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 133 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0133 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0131 | dnan线88杆 | PZXL-00092-N0132 | dnan线89杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 134 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0134 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0212 | dnan线恒鼎支线44杆 | PZXL-00092-N0213 | dnan线恒鼎支线45杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 135 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0135 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0129 | dnan线86杆 | PZXL-00092-N0130 | dnan线87杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 136 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0136 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0168 | dnan线恒鼎支线09杆 | PZXL-00092-N0169 | dnan线恒鼎支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 137 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0137 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0193 | dnan线恒鼎支线34杆 | PZXL-00092-N0194 | dnan线恒鼎支线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 138 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0138 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0181 | dnan线恒鼎支线22杆 | PZXL-00092-N0182 | dnan线恒鼎支线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 139 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0139 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0127 | dnan线84杆 | PZXL-00092-N0128 | dnan线85杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 140 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0140 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0194 | dnan线恒鼎支线35杆 | PZXL-00092-N0204 | dnan线恒鼎支线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 141 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0141 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0206 | dnan线恒鼎支线38杆 | PZXL-00092-N0207 | dnan线恒鼎支线39杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 142 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0142 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0204 | dnan线恒鼎支线36杆 | PZXL-00092-N0205 | dnan线恒鼎支线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 143 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0143 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0120 | dnan线78杆 | PZXL-00092-N0121 | dnan线79杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 144 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0144 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0132 | dnan线89杆 | PZXL-00092-N0133 | dnan线90杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 145 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0145 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0172 | dnan线恒鼎支线13杆 | PZXL-00092-N0173 | dnan线恒鼎支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 146 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0146 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0128 | dnan线85杆 | PZXL-00092-N0129 | dnan线86杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 147 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0147 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0096 | dnan线65杆 | PZXL-00092-N0097 | dnan线66杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 148 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0148 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0089 | dnan线58杆 | PZXL-00092-N0090 | dnan线59杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 149 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0149 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0192 | dnan线恒鼎支线33杆 | PZXL-00092-N0193 | dnan线恒鼎支线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 150 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0150 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0233 | dnan线黄安六支站支线10 | PZXL-00092-N0234 | dnan线黄安六支站支线11 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 151 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0151 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0059 | dnan线39杆 | PZXL-00092-N0060 | dnan线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 152 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0152 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0100 | dnan线69杆 | PZXL-00092-N0101 | dnan线70杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 153 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0153 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0045 | dnan线25杆 | PZXL-00092-N0046 | dnan线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 154 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0154 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0047 | dnan线27杆 | PZXL-00092-N0048 | dnan线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 155 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0155 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0117 | dnan线75杆 | PZXL-00092-N0118 | dnan线76杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 156 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0156 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0018 | dnan线03杆 | PZXL-00092-N0019 | dnan线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 157 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0157 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0169 | dnan线恒鼎支线10杆 | PZXL-00092-N0170 | dnan线恒鼎支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 158 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0158 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0017 | dnan线02杆 | PZXL-00092-N0018 | dnan线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 159 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0159 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0163 | dnan线恒鼎支线04杆 | PZXL-00092-N0164 | dnan线恒鼎支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 160 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0160 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0208 | dnan线恒鼎支线40杆 | PZXL-00092-N0209 | dnan线恒鼎支线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 161 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0161 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0173 | dnan线恒鼎支线14杆 | PZXL-00092-N0174 | dnan线恒鼎支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 162 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0162 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0191 | dnan线恒鼎支线32杆 | PZXL-00092-N0192 | dnan线恒鼎支线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 163 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0163 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0118 | dnan线76杆 | PZXL-00092-N0119 | dnan线77杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 164 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0164 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0097 | dnan线66杆 | PZXL-00092-N0098 | dnan线67杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 165 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0165 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0019 | dnan线04杆 | PZXL-00092-N0020 | dnan线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 166 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0166 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0161 | dnan线恒鼎支线02杆 | PZXL-00092-N0162 | dnan线恒鼎支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 167 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0167 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0053 | dnan线33杆 | PZXL-00092-N0054 | dnan线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 168 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0168 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0142 | dnan线99杆 | PZXL-00092-N0026 | dnan线100杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 169 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0169 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0044 | dnan线24杆 | PZXL-00092-N0045 | dnan线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 170 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0170 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0188 | dnan线恒鼎支线29杆 | PZXL-00092-N0189 | dnan线恒鼎支线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 171 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0171 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0171 | dnan线恒鼎支线12杆 | PZXL-00092-N0172 | dnan线恒鼎支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 172 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0172 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0170 | dnan线恒鼎支线11杆 | PZXL-00092-N0171 | dnan线恒鼎支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 173 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0173 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0215 | dnan线恒鼎支线47杆 | PZXL-00092-N0216 | dnan线恒鼎支线48杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 174 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0174 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0162 | dnan线恒鼎支线03杆 | PZXL-00092-N0163 | dnan线恒鼎支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 175 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0175 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0180 | dnan线恒鼎支线21杆 | PZXL-00092-N0181 | dnan线恒鼎支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 176 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0176 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0189 | dnan线恒鼎支线30杆 | PZXL-00092-N0190 | dnan线恒鼎支线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 177 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0177 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0115 | dnan线73杆 | PZXL-00092-N0116 | dnan线74杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 178 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0178 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0166 | dnan线恒鼎支线07杆 | PZXL-00092-N0167 | dnan线恒鼎支线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 179 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0179 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0051 | dnan线31杆 | PZXL-00092-N0052 | dnan线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 180 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0180 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0214 | dnan线恒鼎支线46杆 | PZXL-00092-N0215 | dnan线恒鼎支线47杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 181 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0181 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0098 | dnan线67杆 | PZXL-00092-N0099 | dnan线68杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 182 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0182 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0121 | dnan线79杆 | PZXL-00092-N0122 | dnan线80杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 183 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0183 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0175 | dnan线恒鼎支线16杆 | PZXL-00092-N0176 | dnan线恒鼎支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 184 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0184 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0178 | dnan线恒鼎支线19杆 | PZXL-00092-N0179 | dnan线恒鼎支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 185 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0185 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0099 | dnan线68杆 | PZXL-00092-N0100 | dnan线69杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 186 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0186 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0186 | dnan线恒鼎支线27杆 | PZXL-00092-N0187 | dnan线恒鼎支线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 187 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0187 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0123 | dnan线81杆 | PZXL-00092-N0125 | dnan线82杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 188 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0188 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0160 | dnan线恒鼎支线01杆 | PZXL-00092-N0161 | dnan线恒鼎支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 189 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0189 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0205 | dnan线恒鼎支线37杆 | PZXL-00092-N0206 | dnan线恒鼎支线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 190 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0190 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0026 | dnan线100杆 | PZXL-00092-N0027 | dnan线101杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 191 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0191 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0190 | dnan线恒鼎支线31杆 | PZXL-00092-N0191 | dnan线恒鼎支线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 192 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0192 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0144 | dnan线合金厂支线2杆 | PZXL-00092-N0145 | dnan线合金厂支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 193 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0193 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0124 | dnan线82-1 | PZXL-00092-N0007 | dji南台支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 194 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0194 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0007 | dji南台支线1杆 | PZXL-00092-N0008 | dji南台支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 195 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0195 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0014 | dji南台支线8杆 | PZXL-00092-N0015 | dji南台支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 196 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0196 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0265 | 波士达支线3杆 | PZXL-00092-N0266 | 波士达支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 197 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0197 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0012 | dji南台支线6杆 | PZXL-00092-N0013 | dji南台支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 198 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0198 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0010 | dji南台支线4杆 | PZXL-00092-N0011 | dji南台支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 199 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0199 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0011 | dji南台支线5杆 | PZXL-00092-N0012 | dji南台支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 200 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0200 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0125 | dnan线82杆 | PZXL-00092-N0124 | dnan线82-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 201 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0201 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0264 | 波士达支线2杆 | PZXL-00092-N0265 | 波士达支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 202 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0202 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0013 | dji南台支线7杆 | PZXL-00092-N0014 | dji南台支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 203 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0203 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0145 | dnan线合金厂支线3杆 | PZXL-00092-N0146 | dnan线合金厂支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 204 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0204 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0124 | dnan线82-1 | PZXL-00092-N0126 | dnan线83杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 205 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0205 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0008 | dji南台支线2杆 | PZXL-00092-N0009 | dji南台支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 206 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0206 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0041 | dnan线21杆 | PZXL-00092-N0263 | 波士达支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 207 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0207 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0009 | dji南台支线3杆 | PZXL-00092-N0010 | dji南台支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 208 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0208 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0109 | dnan线73-4 | PZXL-00092-N0110 | dnan线73-5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 209 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0209 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0111 | dnan线73-6 | PZXL-00092-N0112 | dnan线73-7 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 210 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0210 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0108 | dnan线73-3 | PZXL-00092-N0109 | dnan线73-4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 211 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0211 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0112 | dnan线73-7 | PZXL-00092-N0113 | dnan线73-8 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 212 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0212 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0104 | dnan线73-1 | PZXL-00092-N0107 | dnan线73-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 213 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0213 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0105 | dnan线73-10 | PZXL-00092-N0106 | dnan线73-11 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 214 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0214 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0115 | dnan线73杆 | PZXL-00092-N0104 | dnan线73-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 215 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0215 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0110 | dnan线73-5 | PZXL-00092-N0111 | dnan线73-6 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 216 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0216 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0113 | dnan线73-8 | PZXL-00092-N0114 | dnan线73-9 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 217 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0217 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0114 | dnan线73-9 | PZXL-00092-N0105 | dnan线73-10 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 218 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0218 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0107 | dnan线73-2 | PZXL-00092-N0108 | dnan线73-3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 219 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0219 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0156 | dnan线天齐七支站支线10 | PZXL-00092-N0157 | dnan线天齐七支站支线11 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 220 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0220 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0155 | dnan线天齐七支站支线09杆 | PZXL-00092-N0268 | 金凤凰1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 221 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0221 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0158 | dnan线天齐七支站支线12 | PZXL-00092-N0159 | dnan线天齐七支站支线13 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 222 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0222 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0155 | dnan线天齐七支站支线09杆 | PZXL-00092-N0156 | dnan线天齐七支站支线10 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 223 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0223 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0268 | 金凤凰1 | PZXL-00092-N0269 | 金凤凰2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 224 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0224 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0157 | dnan线天齐七支站支线11 | PZXL-00092-N0158 | dnan线天齐七支站支线12 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 225 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0225 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0198 | dnan线恒鼎支线35杆-4 | PZXL-00092-N0199 | dnan线恒鼎支线35杆-5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 226 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0226 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0195 | dnan线恒鼎支线35杆-1 | PZXL-00092-N0196 | dnan线恒鼎支线35杆-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 227 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0227 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0202 | dnan线恒鼎支线35杆-8 | PZXL-00092-N0203 | dnan线恒鼎支线35杆-9 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 228 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0228 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0256 | 国成支线4 | PZXL-00092-N0257 | 国成支线5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 229 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0229 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0200 | dnan线恒鼎支线35杆-6 | PZXL-00092-N0201 | dnan线恒鼎支线35杆-7 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 230 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0230 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0194 | dnan线恒鼎支线35杆 | PZXL-00092-N0195 | dnan线恒鼎支线35杆-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 231 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0231 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0199 | dnan线恒鼎支线35杆-5 | PZXL-00092-N0200 | dnan线恒鼎支线35杆-6 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 232 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0232 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0253 | 国成支线1 | PZXL-00092-N0254 | 国成支线2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 233 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0233 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0046 | dnan线26杆 | PZXL-00092-N0253 | 国成支线1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 234 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0234 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0201 | dnan线恒鼎支线35杆-7 | PZXL-00092-N0202 | dnan线恒鼎支线35杆-8 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 235 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0235 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0255 | 国成支线3 | PZXL-00092-N0256 | 国成支线4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 236 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0236 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0196 | dnan线恒鼎支线35杆-2 | PZXL-00092-N0197 | dnan线恒鼎支线35杆-3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 237 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0237 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0254 | 国成支线2 | PZXL-00092-N0255 | 国成支线3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 238 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0238 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0197 | dnan线恒鼎支线35杆-3 | PZXL-00092-N0198 | dnan线恒鼎支线35杆-4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 239 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0239 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0068 | dnan线46杆 | PZXL-00092-N0066 | dnan线46-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 240 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0240 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0242 | dnan线黄安六支站支线9-1杆 | PZXL-00092-N0251 | 刘一刀支线1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 241 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0241 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0066 | dnan线46-1 | PZXL-00092-N0067 | dnan线46-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 242 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0242 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0237 | dnan线黄安六支站支线14 | PZXL-00092-N0238 | dnan线黄安六支站支线15 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 243 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0243 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0259 | 大晶支线2 | PZXL-00092-N0260 | 大晶支线3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 244 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0244 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0240 | dnan线黄安六支站支线17 | PZXL-00092-N0241 | dnan线黄安六支站支线18 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 245 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0245 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0258 | 大晶支线1 | PZXL-00092-N0259 | 大晶支线2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 246 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0246 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0085 | dnan线56-1 | PZXL-00092-N0086 | dnan线56-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 247 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0247 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0087 | dnan线56杆 | PZXL-00092-N0085 | dnan线56-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 248 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0248 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0095 | dnan线64杆 | PZXL-00092-N0258 | 大晶支线1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 249 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0249 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0260 | 大晶支线3 | PZXL-00092-N0261 | 大晶支线4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 250 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0250 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0247 | 军霞器材支线5 | PZXL-00092-N0248 | 军霞器材支线6 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 251 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0251 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0248 | 军霞器材支线6 | PZXL-00092-N0249 | 军霞器材支线7 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 252 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0252 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0249 | 军霞器材支线7 | PZXL-00092-N0250 | 军霞器材支线8 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 253 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0253 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0245 | 军霞器材支线3 | PZXL-00092-N0246 | 军霞器材支线4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 254 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0254 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0246 | 军霞器材支线4 | PZXL-00092-N0247 | 军霞器材支线5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 255 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0255 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0244 | 军霞器材支线2 | PZXL-00092-N0245 | 军霞器材支线3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 256 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0256 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0243 | 军霞器材支线1杆 | PZXL-00092-N0244 | 军霞器材支线2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 257 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0257 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0239 | dnan线黄安六支站支线16 | PZXL-00092-N0240 | dnan线黄安六支站支线17 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 258 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0258 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0236 | dnan线黄安六支站支线13 | PZXL-00092-N0237 | dnan线黄安六支站支线14 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 259 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0259 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0238 | dnan线黄安六支站支线15 | PZXL-00092-N0239 | dnan线黄安六支站支线16 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 260 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0260 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0075 | dnan线53-1 | PZXL-00092-N0076 | dnan线53-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 261 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0261 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0076 | dnan线53-2 | PZXL-00092-N0077 | dnan线53-3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 262 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0262 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0079 | dnan线53-5 | PZXL-00092-N0080 | dnan线53-6 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 263 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0263 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0082 | dnan线53杆 | PZXL-00092-N0075 | dnan线53-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 264 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0264 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0077 | dnan线53-3 | PZXL-00092-N0078 | dnan线53-4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 265 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0265 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0080 | dnan线53-6 | PZXL-00092-N0081 | dnan线53-7 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 266 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0266 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0078 | dnan线53-4 | PZXL-00092-N0079 | dnan线53-5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 267 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00092-B0267 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | PZXL-00092-N0266 | 波士达支线4杆 | PZXL-00092-N0267 | 波士达支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 268 | 邳州_10kVdnan线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0001 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0056 | dzhen线北支线10杆 | PZXL-00099-N0057 | dzhen线北支线11杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 2 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0002 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0156 | 王场湖支线1杆 | PZXL-00099-N0160 | 王场湖支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 3 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0003 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0154 | 王场湖支线18杆 | PZXL-00099-N0155 | 王场湖支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 4 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0004 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0158 | 王场湖支线21杆 | PZXL-00099-N0159 | 王场湖支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 5 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0005 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0155 | 王场湖支线19杆 | PZXL-00099-N0157 | 王场湖支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 6 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0006 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0153 | 王场湖支线17杆 | PZXL-00099-N0154 | 王场湖支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 7 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0007 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0157 | 王场湖支线20杆 | PZXL-00099-N0158 | 王场湖支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 8 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0008 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0150 | 王场湖支线14杆 | PZXL-00099-N0151 | 王场湖支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 9 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0009 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0140 | 海天石化支线4杆 | PZXL-00099-N0141 | 海天石化支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 10 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0010 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0130 | 海天石化支线16杆 | PZXL-00099-N0131 | 海天石化支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 11 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0011 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0152 | 王场湖支线16杆 | PZXL-00099-N0153 | 王场湖支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 12 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0012 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0145 | 海天石化支线9杆 | PZXL-00099-N0124 | 海天石化支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 13 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0013 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0121 | 利峰支线2 | PZXL-00099-N0122 | 利峰支线3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 14 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0014 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0114 | dzhen线污水厂支线8杆 | PZXL-00099-N0115 | dzhen线污水厂支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 15 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0015 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0108 | dzhen线污水厂支线2杆 | PZXL-00099-N0109 | dzhen线污水厂支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 16 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0016 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0131 | 海天石化支线17杆 | PZXL-00099-N0132 | 海天石化支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 17 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0017 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0086 | dzhen线正康支线4杆 | PZXL-00099-N0087 | dzhen线正康支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 18 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0018 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0104 | dzhen线污水厂支线20杆 | PZXL-00099-N0105 | dzhen线污水厂支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 19 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0019 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0079 | dzhen线昊阳支线3杆 | PZXL-00099-N0080 | dzhen线昊阳支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 20 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0020 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0095 | dzhen线污水厂支线13-1杆 | PZXL-00099-N0097 | dzhen线污水厂支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 21 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0021 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0098 | dzhen线污水厂支线15杆 | PZXL-00099-N0099 | dzhen线污水厂支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 22 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0022 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0059 | dzhen线南方永磁支线3杆 | PZXL-00099-N0060 | dzhen线南方永磁支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 23 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0023 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0133 | 海天石化支线19杆 | PZXL-00099-N0116 | dzhen线长运支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 24 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0024 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0149 | 王场湖支线13杆 | PZXL-00099-N0150 | 王场湖支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 25 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0025 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0163 | 王场湖支线5杆 | PZXL-00099-N0164 | 王场湖支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 26 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0026 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0127 | 海天石化支线13杆 | PZXL-00099-N0128 | 海天石化支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 27 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0027 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0109 | dzhen线污水厂支线3杆 | PZXL-00099-N0110 | dzhen线污水厂支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 28 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0028 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0115 | dzhen线污水厂支线9杆 | PZXL-00099-N0092 | dzhen线污水厂支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 29 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0029 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0161 | 王场湖支线3杆 | PZXL-00099-N0162 | 王场湖支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 30 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0030 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0099 | dzhen线污水厂支线16杆 | PZXL-00099-N0100 | dzhen线污水厂支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 31 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0031 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0122 | 利峰支线3 | PZXL-00099-N0123 | 利峰支线4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 32 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0032 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0100 | dzhen线污水厂支线17杆 | PZXL-00099-N0101 | dzhen线污水厂支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 33 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0033 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0096 | dzhen线污水厂支线13杆 | PZXL-00099-N0156 | 王场湖支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 34 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0034 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0096 | dzhen线污水厂支线13杆 | PZXL-00099-N0095 | dzhen线污水厂支线13-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 35 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0035 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0151 | 王场湖支线15杆 | PZXL-00099-N0152 | 王场湖支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 36 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0036 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0113 | dzhen线污水厂支线7杆 | PZXL-00099-N0077 | dzhen线昊阳支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 37 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0037 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0078 | dzhen线昊阳支线2杆 | PZXL-00099-N0079 | dzhen线昊阳支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 38 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0038 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0128 | 海天石化支线14杆 | PZXL-00099-N0129 | 海天石化支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 39 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0039 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0077 | dzhen线昊阳支线1杆 | PZXL-00099-N0078 | dzhen线昊阳支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 40 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0040 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0105 | dzhen线污水厂支线21杆 | PZXL-00099-N0106 | dzhen线污水厂支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 41 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0041 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0106 | dzhen线污水厂支线22杆 | PZXL-00099-N0107 | dzhen线污水厂支线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 42 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0042 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0143 | 海天石化支线7杆 | PZXL-00099-N0144 | 海天石化支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 43 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0043 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0015 | dzhen线15杆 | PZXL-00099-N0016 | dzhen线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 44 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0044 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0024 | dzhen线24杆 | PZXL-00099-N0025 | dzhen线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 45 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0045 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0001 | dzhen线01杆 | PZXL-00099-N0002 | dzhen线02杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 46 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0046 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0006 | dzhen线06杆 | PZXL-00099-N0051 | dzhen线北支线01杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 47 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0047 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0065 | dzhen线恒鼎支线14杆 | PZXL-00099-N0066 | dzhen线恒鼎支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 48 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0048 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0015 | dzhen线15杆 | PZXL-00099-N0120 | 利峰支线1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 49 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0049 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0167 | 王场湖支线9杆 | PZXL-00099-N0146 | 王场湖支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 50 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0050 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0160 | 王场湖支线2杆 | PZXL-00099-N0161 | 王场湖支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 51 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0051 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0166 | 王场湖支线8杆 | PZXL-00099-N0167 | 王场湖支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 52 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0052 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0147 | 王场湖支线11杆 | PZXL-00099-N0148 | 王场湖支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 53 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0053 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0126 | 海天石化支线12杆 | PZXL-00099-N0127 | 海天石化支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 54 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0054 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0093 | dzhen线污水厂支线11杆 | PZXL-00099-N0094 | dzhen线污水厂支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 55 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0055 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0102 | dzhen线污水厂支线19杆 | PZXL-00099-N0104 | dzhen线污水厂支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 56 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0056 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0113 | dzhen线污水厂支线7杆 | PZXL-00099-N0114 | dzhen线污水厂支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 57 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0057 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0162 | 王场湖支线4杆 | PZXL-00099-N0163 | 王场湖支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 58 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0058 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0146 | 王场湖支线10杆 | PZXL-00099-N0147 | 王场湖支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 59 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0059 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0112 | dzhen线污水厂支线6杆 | PZXL-00099-N0113 | dzhen线污水厂支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 60 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0060 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0133 | 海天石化支线19杆 | PZXL-00099-N0135 | 海天石化支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 61 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0061 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0139 | 海天石化支线3杆 | PZXL-00099-N0140 | 海天石化支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 62 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0062 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0083 | dzhen线正康支线1杆 | PZXL-00099-N0084 | dzhen线正康支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 63 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0063 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0134 | 海天石化支线1杆 | PZXL-00099-N0138 | 海天石化支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 64 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0064 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0136 | 海天石化支线21杆 | PZXL-00099-N0137 | 海天石化支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 65 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0065 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0118 | 三仪支线01杆 | PZXL-00099-N0119 | 三仪支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 66 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0066 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0042 | dzhen线41杆 | PZXL-00099-N0043 | dzhen线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 67 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0067 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0045 | dzhen线44杆 | PZXL-00099-N0046 | dzhen线45杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 68 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0068 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0125 | 海天石化支线11杆 | PZXL-00099-N0126 | 海天石化支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 69 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0069 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0148 | 王场湖支线12杆 | PZXL-00099-N0149 | 王场湖支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 70 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0070 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0129 | 海天石化支线15杆 | PZXL-00099-N0130 | 海天石化支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 71 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0071 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0043 | dzhen线42杆 | PZXL-00099-N0044 | dzhen线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 72 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0072 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0141 | 海天石化支线5杆 | PZXL-00099-N0142 | 海天石化支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 73 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0073 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0124 | 海天石化支线10杆 | PZXL-00099-N0125 | 海天石化支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 74 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0074 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0080 | dzhen线昊阳支线4杆 | PZXL-00099-N0081 | dzhen线昊阳支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 75 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0075 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0138 | 海天石化支线2杆 | PZXL-00099-N0139 | 海天石化支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 76 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0076 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0110 | dzhen线污水厂支线4杆 | PZXL-00099-N0111 | dzhen线污水厂支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 77 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0077 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0092 | dzhen线污水厂支线10杆 | PZXL-00099-N0093 | dzhen线污水厂支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 78 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0078 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0164 | 王场湖支线6杆 | PZXL-00099-N0165 | 王场湖支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 79 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0079 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0142 | 海天石化支线6杆 | PZXL-00099-N0143 | 海天石化支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 80 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0080 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0144 | 海天石化支线8杆 | PZXL-00099-N0145 | 海天石化支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 81 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0081 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0116 | dzhen线长运支线01杆 | PZXL-00099-N0117 | dzhen线长运支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 82 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0082 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0094 | dzhen线污水厂支线12杆 | PZXL-00099-N0096 | dzhen线污水厂支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 83 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0083 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0044 | dzhen线43杆 | PZXL-00099-N0045 | dzhen线44杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 84 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0084 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0132 | 海天石化支线18杆 | PZXL-00099-N0133 | 海天石化支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 85 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0085 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0084 | dzhen线正康支线2杆 | PZXL-00099-N0085 | dzhen线正康支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 86 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0086 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0135 | 海天石化支线20杆 | PZXL-00099-N0136 | 海天石化支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 87 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0087 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0111 | dzhen线污水厂支线5杆 | PZXL-00099-N0112 | dzhen线污水厂支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 88 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0088 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0058 | dzhen线南方永磁支线2杆 | PZXL-00099-N0059 | dzhen线南方永磁支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 89 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0089 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0101 | dzhen线污水厂支线18杆 | PZXL-00099-N0102 | dzhen线污水厂支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 90 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0090 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0103 | dzhen线污水厂支线1杆 | PZXL-00099-N0108 | dzhen线污水厂支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 91 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0091 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0165 | 王场湖支线7杆 | PZXL-00099-N0166 | 王场湖支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 92 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0092 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0120 | 利峰支线1 | PZXL-00099-N0121 | 利峰支线2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 93 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0093 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0085 | dzhen线正康支线3杆 | PZXL-00099-N0086 | dzhen线正康支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 94 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0094 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0063 | dzhen线恒鼎支线12杆 | PZXL-00099-N0064 | dzhen线恒鼎支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 95 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0095 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0066 | dzhen线恒鼎支线15杆 | PZXL-00099-N0067 | dzhen线恒鼎支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 96 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0096 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0031 | dzhen线30杆 | PZXL-00099-N0032 | dzhen线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 97 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0097 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0034 | dzhen线33杆 | PZXL-00099-N0035 | dzhen线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 98 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0098 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0011 | dzhen线11杆 | PZXL-00099-N0012 | dzhen线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 99 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0099 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0074 | dzhen线恒鼎支线7杆 | PZXL-00099-N0075 | dzhen线恒鼎支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 100 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0100 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0051 | dzhen线北支线01杆 | PZXL-00099-N0052 | dzhen线北支线02杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 101 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0101 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0019 | dzhen线19杆 | PZXL-00099-N0020 | dzhen线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 102 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0102 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0036 | dzhen线35杆 | PZXL-00099-N0037 | dzhen线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 103 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0103 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0032 | dzhen线31杆 | PZXL-00099-N0033 | dzhen线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 104 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0104 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0020 | dzhen线20杆 | PZXL-00099-N0021 | dzhen线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 105 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0105 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0039 | dzhen线38杆 | PZXL-00099-N0040 | dzhen线39杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 106 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0106 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0037 | dzhen线36杆 | PZXL-00099-N0038 | dzhen线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 107 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0107 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0009 | dzhen线09杆 | PZXL-00099-N0010 | dzhen线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 108 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0108 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0070 | dzhen线恒鼎支线3杆 | PZXL-00099-N0071 | dzhen线恒鼎支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 109 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0109 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0062 | dzhen线恒鼎支线11杆 | PZXL-00099-N0063 | dzhen线恒鼎支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 110 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0110 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0038 | dzhen线37杆 | PZXL-00099-N0039 | dzhen线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 111 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0111 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0035 | dzhen线34杆 | PZXL-00099-N0036 | dzhen线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 112 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0112 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0004 | dzhen线04杆 | PZXL-00099-N0005 | dzhen线05杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 113 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0113 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0023 | dzhen线23杆 | PZXL-00099-N0024 | dzhen线24杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 114 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0114 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0008 | dzhen线08杆 | PZXL-00099-N0009 | dzhen线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 115 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0115 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0040 | dzhen线39杆 | PZXL-00099-N0041 | dzhen线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 116 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0116 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0053 | dzhen线北支线03杆 | PZXL-00099-N0054 | dzhen线北支线04杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 117 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0117 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0073 | dzhen线恒鼎支线6杆 | PZXL-00099-N0074 | dzhen线恒鼎支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 118 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0118 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0072 | dzhen线恒鼎支线5杆 | PZXL-00099-N0073 | dzhen线恒鼎支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 119 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0119 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0021 | dzhen线21杆 | PZXL-00099-N0022 | dzhen线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 120 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0120 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0030 | dzhen线29杆 | PZXL-00099-N0031 | dzhen线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 121 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0121 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0018 | dzhen线18杆 | PZXL-00099-N0019 | dzhen线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 122 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0122 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0005 | dzhen线05杆 | PZXL-00099-N0006 | dzhen线06杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 123 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0123 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0002 | dzhen线02杆 | PZXL-00099-N0003 | dzhen线03杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 124 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0124 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0054 | dzhen线北支线04杆 | PZXL-00099-N0055 | dzhen线北支线05杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 125 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0125 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0003 | dzhen线03杆 | PZXL-00099-N0004 | dzhen线04杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 126 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0126 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0026 | dzhen线26杆 | PZXL-00099-N0027 | dzhen线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 127 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0127 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0016 | dzhen线16杆 | PZXL-00099-N0017 | dzhen线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 128 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0128 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0014 | dzhen线14杆 | PZXL-00099-N0015 | dzhen线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 129 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0129 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0022 | dzhen线22杆 | PZXL-00099-N0023 | dzhen线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 130 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0130 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0069 | dzhen线恒鼎支线2杆 | PZXL-00099-N0070 | dzhen线恒鼎支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 131 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0131 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0017 | dzhen线17杆 | PZXL-00099-N0018 | dzhen线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 132 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0132 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0067 | dzhen线恒鼎支线16杆 | PZXL-00099-N0068 | dzhen线恒鼎支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 133 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0133 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0010 | dzhen线10杆 | PZXL-00099-N0011 | dzhen线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 134 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0134 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0071 | dzhen线恒鼎支线4杆 | PZXL-00099-N0072 | dzhen线恒鼎支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 135 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0135 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0076 | dzhen线恒鼎支线9杆 | PZXL-00099-N0061 | dzhen线恒鼎支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 136 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0136 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0061 | dzhen线恒鼎支线10杆 | PZXL-00099-N0062 | dzhen线恒鼎支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 137 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0137 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0033 | dzhen线32杆 | PZXL-00099-N0034 | dzhen线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 138 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0138 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0025 | dzhen线25杆 | PZXL-00099-N0026 | dzhen线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 139 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0139 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0028 | dzhen线28杆 | PZXL-00099-N0030 | dzhen线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 140 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0140 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0075 | dzhen线恒鼎支线8杆 | PZXL-00099-N0076 | dzhen线恒鼎支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 141 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0141 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0064 | dzhen线恒鼎支线13杆 | PZXL-00099-N0065 | dzhen线恒鼎支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 142 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0142 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0012 | dzhen线12杆 | PZXL-00099-N0013 | dzhen线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 143 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0143 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0052 | dzhen线北支线02杆 | PZXL-00099-N0053 | dzhen线北支线03杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 144 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0144 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0027 | dzhen线27杆 | PZXL-00099-N0028 | dzhen线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 145 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0145 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0041 | dzhen线40杆 | PZXL-00099-N0042 | dzhen线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 146 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0146 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0013 | dzhen线13杆 | PZXL-00099-N0014 | dzhen线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 147 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0147 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0049 | dzhen线力达支线3杆 | PZXL-00099-N0050 | dzhen线力达支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 148 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0148 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0110 | dzhen线污水厂支线4杆 | PZXL-00099-N0047 | dzhen线力达支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 149 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0149 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0047 | dzhen线力达支线1杆 | PZXL-00099-N0048 | dzhen线力达支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 150 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0150 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0048 | dzhen线力达支线2杆 | PZXL-00099-N0049 | dzhen线力达支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 151 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0151 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0061 | dzhen线恒鼎支线10杆 | PZXL-00099-N0083 | dzhen线正康支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 152 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0152 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0034 | dzhen线33杆 | PZXL-00099-N0118 | 三仪支线01杆 | 50.0 | JKLYJ-240/10 | JKLYJ-10-240 (raw写法与典型库JKLYJ-240/10等价) | A/B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 153 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0153 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0015 | dzhen线15杆 | PZXL-00099-N0134 | 海天石化支线1杆 | 50.0 | JKLYJ-240/10 | JKLYJ-10-240 (raw写法与典型库JKLYJ-240/10等价) | A/B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 154 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0154 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0006 | dzhen线06杆 | PZXL-00099-N0007 | dzhen线07杆 | 50.0 | JKLGYJ-70 | JKLGYJ-10-70/10 | B | 0.443 | 0.397 | 0.02215 | 0.01985 | 245.0 | 247.5 | 4.2435 | CLOSED | 155 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 245 | 4.2435 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0155 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0097 | dzhen线污水厂支线14杆 | PZXL-00099-N0098 | dzhen线污水厂支线15杆 | 50.0 | JKLYJ-240/10 | JKLYJ-10-240 (raw写法与典型库JKLYJ-240/10等价) | A/B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 156 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0156 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0090 | dzhen线正康支线8杆 | PZXL-00099-N0091 | dzhen线正康支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 157 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0157 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0088 | dzhen线正康支线6杆 | PZXL-00099-N0089 | dzhen线正康支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 158 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0158 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0091 | dzhen线正康支线9杆 | PZXL-00099-N0082 | dzhen线正康支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 159 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0159 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0089 | dzhen线正康支线7杆 | PZXL-00099-N0090 | dzhen线正康支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 160 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0160 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0087 | dzhen线正康支线5杆 | PZXL-00099-N0088 | dzhen线正康支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 161 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00099-B0161 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | PZXL-00099-N0030 | dzhen线29杆 | PZXL-00099-N0029 | dzhen线29-1 | 50.0 | JLRX/T-120/30 | JLRX/T-120/30 (碳纤维复合芯耐热导线家族) | C-PROXY | 0.33 | 0.38 | 0.0165 | 0.019 | 300.0 | 350.0 | 5.1962 | CLOSED | 162 | 邳州_10kV墩振线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 300 | 5.1962 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0001 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0191 | dxi线王场湖支线7-4 | PZXL-00097-N0192 | dxi线王场湖支线7-5 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 2 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0002 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0189 | dxi线王场湖支线7-2 | PZXL-00097-N0190 | dxi线王场湖支线7-3 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 3 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0003 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0180 | dxi线王场湖支线07 | PZXL-00097-N0188 | dxi线王场湖支线7-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 4 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0004 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0190 | dxi线王场湖支线7-3 | PZXL-00097-N0191 | dxi线王场湖支线7-4 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 5 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0005 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0188 | dxi线王场湖支线7-1 | PZXL-00097-N0189 | dxi线王场湖支线7-2 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 6 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0006 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0089 | dxi线44杆 | PZXL-00097-N0088 | dxi线44-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 7 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0007 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0049 | dxi线06杆 | PZXL-00097-N0050 | dxi线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 8 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0008 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0182 | dxi线王场湖支线09 | PZXL-00097-N0193 | dxi线高速路变支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 9 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0009 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0160 | dxi线海天石化支线31 | PZXL-00097-N0107 | dxi线兴春支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 10 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0010 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0170 | dxi线海天石化支线41杆 | PZXL-00097-N0171 | dxi线海天石化支线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 11 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0011 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0108 | dxi线兴春支线02杆 | PZXL-00097-N0109 | dxi线兴春支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 12 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0012 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0172 | dxi线海天石化支线43杆 | PZXL-00097-N0173 | dxi线海天石化支线44杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 13 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0013 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0169 | dxi线海天石化支线40杆 | PZXL-00097-N0170 | dxi线海天石化支线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 14 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0014 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0109 | dxi线兴春支线03杆 | PZXL-00097-N0110 | dxi线兴春支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 15 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0015 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0049 | dxi线06杆 | PZXL-00097-N0011 | dxi北支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 16 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0016 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0171 | dxi线海天石化支线42杆 | PZXL-00097-N0172 | dxi线海天石化支线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 17 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0017 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0107 | dxi线兴春支线01杆 | PZXL-00097-N0108 | dxi线兴春支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 18 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0018 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0166 | dxi线海天石化支线37 | PZXL-00097-N0174 | dxi线王场湖支线01 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 19 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0019 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0052 | dxi线09杆 | PZXL-00097-N0053 | dxi线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 20 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0020 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0058 | dxi线14杆 | PZXL-00097-N0059 | dxi线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 21 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0021 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0051 | dxi线08杆 | PZXL-00097-N0052 | dxi线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 22 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0022 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0057 | dxi线13杆 | PZXL-00097-N0058 | dxi线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 23 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0023 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0043 | dxi北支线9杆 | PZXL-00097-N0001 | dxi北支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 24 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0024 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0064 | dxi线20杆 | PZXL-00097-N0065 | dxi线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 25 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0025 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0055 | dxi线12杆 | PZXL-00097-N0057 | dxi线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 26 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0026 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0042 | dxi北支线8杆 | PZXL-00097-N0043 | dxi北支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 27 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0027 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0033 | dxi北支线3杆 | PZXL-00097-N0038 | dxi北支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 28 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0028 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0060 | dxi线16杆 | PZXL-00097-N0061 | dxi线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 29 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0029 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0053 | dxi线10杆 | PZXL-00097-N0054 | dxi线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 30 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0030 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0046 | dxi线03杆 | PZXL-00097-N0047 | dxi线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 31 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0031 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0054 | dxi线11杆 | PZXL-00097-N0055 | dxi线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 32 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0032 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0140 | dxi线海天石化支线11 | PZXL-00097-N0141 | dxi线海天石化支线12 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 33 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0033 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0143 | dxi线海天石化支线14 | PZXL-00097-N0144 | dxi线海天石化支线15 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 34 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0034 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0174 | dxi线王场湖支线01 | PZXL-00097-N0175 | dxi线王场湖支线02 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 35 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0035 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0176 | dxi线王场湖支线03 | PZXL-00097-N0177 | dxi线王场湖支线04 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 36 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0036 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0179 | dxi线王场湖支线06 | PZXL-00097-N0180 | dxi线王场湖支线07 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 37 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0037 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0185 | dxi线王场湖支线12 | PZXL-00097-N0186 | dxi线王场湖支线13 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 38 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0038 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0184 | dxi线王场湖支线11 | PZXL-00097-N0185 | dxi线王场湖支线12 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 39 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0039 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0160 | dxi线海天石化支线31 | PZXL-00097-N0161 | dxi线海天石化支线32 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 40 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0040 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0166 | dxi线海天石化支线37 | PZXL-00097-N0167 | dxi线海天石化支线38 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 41 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0041 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0134 | dxi线海天石化支线05 | PZXL-00097-N0135 | dxi线海天石化支线06 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 42 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0042 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0145 | dxi线海天石化支线16 | PZXL-00097-N0146 | dxi线海天石化支线17 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 43 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0043 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0165 | dxi线海天石化支线36 | PZXL-00097-N0166 | dxi线海天石化支线37 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 44 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0044 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0168 | dxi线海天石化支线39 | PZXL-00097-N0169 | dxi线海天石化支线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 45 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0045 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0070 | dxi线26杆 | PZXL-00097-N0071 | dxi线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 46 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0046 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0002 | dxi北支线11杆 | PZXL-00097-N0003 | dxi北支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 47 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0047 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0005 | dxi北支线14杆 | PZXL-00097-N0006 | dxi北支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 48 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0048 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0016 | dxi北支线24杆 | PZXL-00097-N0017 | dxi北支线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 49 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0049 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0078 | dxi线34杆 | PZXL-00097-N0079 | dxi线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 50 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0050 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0021 | dxi北支线29杆 | PZXL-00097-N0023 | dxi北支线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 51 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0051 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0010 | dxi北支线19杆 | PZXL-00097-N0012 | dxi北支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 52 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0052 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0130 | dxi线海天石化支线01 | PZXL-00097-N0131 | dxi线海天石化支线02 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 53 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0053 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0075 | dxi线31杆 | PZXL-00097-N0076 | dxi线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 54 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0054 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0082 | dxi线38杆 | PZXL-00097-N0083 | dxi线39杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 55 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0055 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0027 | dxi北支线34杆 | PZXL-00097-N0028 | dxi北支线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 56 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0056 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0029 | dxi北支线36杆 | PZXL-00097-N0030 | dxi北支线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 57 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0057 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0020 | dxi北支线28杆 | PZXL-00097-N0021 | dxi北支线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 58 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0058 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0026 | dxi北支线33杆 | PZXL-00097-N0027 | dxi北支线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 59 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0059 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0031 | dxi北支线38杆 | PZXL-00097-N0032 | dxi北支线39杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 60 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0060 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0163 | dxi线海天石化支线34 | PZXL-00097-N0164 | dxi线海天石化支线35 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 61 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0061 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0182 | dxi线王场湖支线09 | PZXL-00097-N0183 | dxi线王场湖支线10 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 62 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0062 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0139 | dxi线海天石化支线10 | PZXL-00097-N0140 | dxi线海天石化支线11 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 63 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0063 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0186 | dxi线王场湖支线13 | PZXL-00097-N0187 | dxi线王场湖支线14 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 64 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0064 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0149 | dxi线海天石化支线20 | PZXL-00097-N0150 | dxi线海天石化支线21 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 65 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0065 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0157 | dxi线海天石化支线28 | PZXL-00097-N0158 | dxi线海天石化支线29 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 66 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0066 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0024 | dxi北支线31杆 | PZXL-00097-N0025 | dxi北支线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 67 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0067 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0161 | dxi线海天石化支线32 | PZXL-00097-N0162 | dxi线海天石化支线33 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 68 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0068 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0162 | dxi线海天石化支线33 | PZXL-00097-N0163 | dxi线海天石化支线34 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 69 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0069 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0007 | dxi北支线16杆 | PZXL-00097-N0008 | dxi北支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 70 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0070 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0074 | dxi线30杆 | PZXL-00097-N0075 | dxi线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 71 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0071 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0076 | dxi线32杆 | PZXL-00097-N0077 | dxi线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 72 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0072 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0183 | dxi线王场湖支线10 | PZXL-00097-N0184 | dxi线王场湖支线11 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 73 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0073 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0177 | dxi线王场湖支线04 | PZXL-00097-N0178 | dxi线王场湖支线05 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 74 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0074 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0153 | dxi线海天石化支线24 | PZXL-00097-N0154 | dxi线海天石化支线25 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 75 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0075 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0137 | dxi线海天石化支线08 | PZXL-00097-N0138 | dxi线海天石化支线09 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 76 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0076 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0141 | dxi线海天石化支线12 | PZXL-00097-N0142 | dxi线海天石化支线13 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 77 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0077 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0146 | dxi线海天石化支线17 | PZXL-00097-N0147 | dxi线海天石化支线18 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 78 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0078 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0008 | dxi北支线17杆 | PZXL-00097-N0009 | dxi北支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 79 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0079 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0017 | dxi北支线25杆 | PZXL-00097-N0018 | dxi北支线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 80 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0080 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0073 | dxi线29杆 | PZXL-00097-N0074 | dxi线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 81 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0081 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0083 | dxi线39杆 | PZXL-00097-N0084 | dxi线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 82 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0082 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0018 | dxi北支线26杆 | PZXL-00097-N0019 | dxi北支线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 83 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0083 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0059 | dxi线15杆 | PZXL-00097-N0130 | dxi线海天石化支线01 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 84 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0084 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0132 | dxi线海天石化支线03 | PZXL-00097-N0133 | dxi线海天石化支线04 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 85 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0085 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0036 | dxi北支线42杆 | PZXL-00097-N0037 | dxi北支线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 86 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0086 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0014 | dxi北支线22杆 | PZXL-00097-N0015 | dxi北支线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 87 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0087 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0015 | dxi北支线23杆 | PZXL-00097-N0016 | dxi北支线24杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 88 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0088 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0180 | dxi线王场湖支线07 | PZXL-00097-N0181 | dxi线王场湖支线08 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 89 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0089 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0079 | dxi线35杆 | PZXL-00097-N0080 | dxi线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 90 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0090 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0081 | dxi线37杆 | PZXL-00097-N0082 | dxi线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 91 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0091 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0023 | dxi北支线30杆 | PZXL-00097-N0024 | dxi北支线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 92 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0092 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0167 | dxi线海天石化支线38 | PZXL-00097-N0168 | dxi线海天石化支线39 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 93 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0093 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0131 | dxi线海天石化支线02 | PZXL-00097-N0132 | dxi线海天石化支线03 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 94 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0094 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0136 | dxi线海天石化支线07 | PZXL-00097-N0137 | dxi线海天石化支线08 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 95 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0095 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0156 | dxi线海天石化支线27 | PZXL-00097-N0157 | dxi线海天石化支线28 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 96 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0096 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0158 | dxi线海天石化支线29 | PZXL-00097-N0159 | dxi线海天石化支线30 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 97 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0097 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0013 | dxi北支线21杆 | PZXL-00097-N0014 | dxi北支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 98 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0098 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0133 | dxi线海天石化支线04 | PZXL-00097-N0134 | dxi线海天石化支线05 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 99 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0099 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0155 | dxi线海天石化支线26 | PZXL-00097-N0156 | dxi线海天石化支线27 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 100 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0100 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0085 | dxi线41杆 | PZXL-00097-N0086 | dxi线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 101 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0101 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0039 | dxi北支线5杆 | PZXL-00097-N0040 | dxi北支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 102 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0102 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0044 | dxi线01杆 | PZXL-00097-N0045 | dxi线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 103 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0103 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0175 | dxi线王场湖支线02 | PZXL-00097-N0176 | dxi线王场湖支线03 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 104 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0104 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0138 | dxi线海天石化支线09 | PZXL-00097-N0139 | dxi线海天石化支线10 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 105 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0105 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0142 | dxi线海天石化支线13 | PZXL-00097-N0143 | dxi线海天石化支线14 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 106 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0106 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0148 | dxi线海天石化支线19 | PZXL-00097-N0149 | dxi线海天石化支线20 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 107 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0107 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0164 | dxi线海天石化支线35 | PZXL-00097-N0165 | dxi线海天石化支线36 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 108 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0108 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0152 | dxi线海天石化支线23 | PZXL-00097-N0153 | dxi线海天石化支线24 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 109 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0109 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0009 | dxi北支线18杆 | PZXL-00097-N0010 | dxi北支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 110 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0110 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0025 | dxi北支线32杆 | PZXL-00097-N0026 | dxi北支线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 111 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0111 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0077 | dxi线33杆 | PZXL-00097-N0078 | dxi线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 112 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0112 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0080 | dxi线36杆 | PZXL-00097-N0081 | dxi线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 113 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0113 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0012 | dxi北支线20杆 | PZXL-00097-N0013 | dxi北支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 114 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0114 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0019 | dxi北支线27杆 | PZXL-00097-N0020 | dxi北支线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 115 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0115 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0028 | dxi北支线35杆 | PZXL-00097-N0029 | dxi北支线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 116 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0116 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0071 | dxi线27杆 | PZXL-00097-N0072 | dxi线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 117 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0117 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0003 | dxi北支线12杆 | PZXL-00097-N0004 | dxi北支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 118 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0118 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0030 | dxi北支线37杆 | PZXL-00097-N0031 | dxi北支线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 119 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0119 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0084 | dxi线40杆 | PZXL-00097-N0085 | dxi线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 120 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0120 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0004 | dxi北支线13杆 | PZXL-00097-N0005 | dxi北支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 121 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0121 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0181 | dxi线王场湖支线08 | PZXL-00097-N0182 | dxi线王场湖支线09 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 122 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0122 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0147 | dxi线海天石化支线18 | PZXL-00097-N0148 | dxi线海天石化支线19 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 123 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0123 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0154 | dxi线海天石化支线25 | PZXL-00097-N0155 | dxi线海天石化支线26 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 124 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0124 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0150 | dxi线海天石化支线21 | PZXL-00097-N0151 | dxi线海天石化支线22 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 125 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0125 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0151 | dxi线海天石化支线22 | PZXL-00097-N0152 | dxi线海天石化支线23 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 126 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0126 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0144 | dxi线海天石化支线15 | PZXL-00097-N0145 | dxi线海天石化支线16 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 127 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0127 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0159 | dxi线海天石化支线30 | PZXL-00097-N0160 | dxi线海天石化支线31 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 128 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0128 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0069 | dxi线25杆 | PZXL-00097-N0070 | dxi线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 129 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0129 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0032 | dxi北支线39杆 | PZXL-00097-N0034 | dxi北支线40杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 130 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0130 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0034 | dxi北支线40杆 | PZXL-00097-N0035 | dxi北支线41杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 131 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0131 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0072 | dxi线28杆 | PZXL-00097-N0073 | dxi线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 132 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0132 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0135 | dxi线海天石化支线06 | PZXL-00097-N0136 | dxi线海天石化支线07 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 133 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0133 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0006 | dxi北支线15杆 | PZXL-00097-N0007 | dxi北支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 134 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0134 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0178 | dxi线王场湖支线05 | PZXL-00097-N0179 | dxi线王场湖支线06 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 135 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0135 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0035 | dxi北支线41杆 | PZXL-00097-N0036 | dxi北支线42杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 136 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0136 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0059 | dxi线15杆 | PZXL-00097-N0060 | dxi线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 137 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0137 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0068 | dxi线24杆 | PZXL-00097-N0069 | dxi线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 138 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0138 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0112 | dxi线合金厂支线01杆 | PZXL-00097-N0113 | dxi线合金厂支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 139 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0139 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0102 | dxi线企服中心支线5杆 | PZXL-00097-N0103 | dxi线企服中心支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 140 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0140 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0094 | dxi线企服中心支线14杆 | PZXL-00097-N0095 | dxi线企服中心支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 141 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0141 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0101 | dxi线企服中心支线4杆 | PZXL-00097-N0102 | dxi线企服中心支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 142 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0142 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0068 | dxi线24杆 | PZXL-00097-N0098 | dxi线企服中心支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 143 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0143 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0091 | dxi线企服中心支线11杆 | PZXL-00097-N0092 | dxi线企服中心支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 144 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0144 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0090 | dxi线企服中心支线10杆 | PZXL-00097-N0091 | dxi线企服中心支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 145 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0145 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0098 | dxi线企服中心支线1杆 | PZXL-00097-N0099 | dxi线企服中心支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 146 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0146 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0105 | dxi线企服中心支线8杆 | PZXL-00097-N0106 | dxi线企服中心支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 147 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0147 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0092 | dxi线企服中心支线12杆 | PZXL-00097-N0093 | dxi线企服中心支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 148 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0148 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0095 | dxi线企服中心支线15杆 | PZXL-00097-N0096 | dxi线企服中心支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 149 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0149 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0099 | dxi线企服中心支线2杆 | PZXL-00097-N0100 | dxi线企服中心支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 150 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0150 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0103 | dxi线企服中心支线6杆 | PZXL-00097-N0104 | dxi线企服中心支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 151 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0151 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0104 | dxi线企服中心支线7杆 | PZXL-00097-N0105 | dxi线企服中心支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 152 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0152 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0100 | dxi线企服中心支线3杆 | PZXL-00097-N0101 | dxi线企服中心支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 153 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0153 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0106 | dxi线企服中心支线9杆 | PZXL-00097-N0090 | dxi线企服中心支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 154 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0154 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0096 | dxi线企服中心支线16杆 | PZXL-00097-N0097 | dxi线企服中心支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 155 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0155 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0093 | dxi线企服中心支线13杆 | PZXL-00097-N0094 | dxi线企服中心支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 156 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0156 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0001 | dxi北支线10杆 | PZXL-00097-N0002 | dxi北支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 157 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0157 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0144 | dxi线海天石化支线15 | PZXL-00097-N0112 | dxi线合金厂支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 158 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0158 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0045 | dxi线02杆 | PZXL-00097-N0046 | dxi线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 159 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0159 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0011 | dxi北支线1杆 | PZXL-00097-N0022 | dxi北支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 160 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0160 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0086 | dxi线42杆 | PZXL-00097-N0087 | dxi线43杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 161 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0161 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0041 | dxi北支线7杆 | PZXL-00097-N0042 | dxi北支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 162 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0162 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0038 | dxi北支线4杆 | PZXL-00097-N0039 | dxi北支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 163 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0163 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0048 | dxi线05杆 | PZXL-00097-N0049 | dxi线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 164 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0164 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0050 | dxi线07杆 | PZXL-00097-N0051 | dxi线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 165 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0165 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0065 | dxi线21杆 | PZXL-00097-N0066 | dxi线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 166 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0166 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0063 | dxi线19杆 | PZXL-00097-N0064 | dxi线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 167 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0167 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0087 | dxi线43杆 | PZXL-00097-N0089 | dxi线44杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 168 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0168 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0040 | dxi北支线6杆 | PZXL-00097-N0041 | dxi北支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 169 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0169 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0047 | dxi线04杆 | PZXL-00097-N0048 | dxi线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 170 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0170 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0066 | dxi线22杆 | PZXL-00097-N0067 | dxi线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 171 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0171 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0022 | dxi北支线2杆 | PZXL-00097-N0033 | dxi北支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 172 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0172 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0062 | dxi线18杆 | PZXL-00097-N0063 | dxi线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 173 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0173 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0061 | dxi线17杆 | PZXL-00097-N0062 | dxi线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 174 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0174 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0057 | dxi线13杆 | PZXL-00097-N0056 | dxi线13-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 175 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0175 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0031 | dxi北支线38杆 | PZXL-00097-N0111 | dxi线北支线38-1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 176 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0176 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0118 | dxi线国成支线4杆 | PZXL-00097-N0119 | dxi线国成支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 177 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0177 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0117 | dxi线国成支线3杆 | PZXL-00097-N0118 | dxi线国成支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 178 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0178 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0121 | dxi线国成支线7杆 | PZXL-00097-N0122 | dxi线国成支线8杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 179 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0179 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0120 | dxi线国成支线6杆 | PZXL-00097-N0121 | dxi线国成支线7杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 180 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0180 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0122 | dxi线国成支线8杆 | PZXL-00097-N0123 | dxi线国成支线9杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 181 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0181 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0119 | dxi线国成支线5杆 | PZXL-00097-N0120 | dxi线国成支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 182 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0182 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0123 | dxi线国成支线9杆 | PZXL-00097-N0114 | dxi线国成支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 183 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0183 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0116 | dxi线国成支线2杆 | PZXL-00097-N0117 | dxi线国成支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 184 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0184 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0115 | dxi线国成支线1杆 | PZXL-00097-N0116 | dxi线国成支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 185 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0185 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0144 | dxi线海天石化支线15 | PZXL-00097-N0115 | dxi线国成支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 186 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0186 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0127 | dxi线日托支线4杆 | PZXL-00097-N0128 | dxi线日托支线5杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 187 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0187 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0089 | dxi线44杆 | PZXL-00097-N0124 | dxi线日托支线1杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 188 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0188 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0126 | dxi线日托支线3杆 | PZXL-00097-N0127 | dxi线日托支线4杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 189 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0189 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0125 | dxi线日托支线2杆 | PZXL-00097-N0126 | dxi线日托支线3杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 190 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0190 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0128 | dxi线日托支线5杆 | PZXL-00097-N0129 | dxi线日托支线6杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 191 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00097-B0191 | PHYSICAL_SPAN | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | PZXL-00097-N0124 | dxi线日托支线1杆 | PZXL-00097-N0125 | dxi线日托支线2杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 192 | 邳州_10kV墩西线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 485 | 485 | 8.4004 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0001 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0042 | hdong线44杆 | PZXL-00154-N0168 | 河湾1#支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 2 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0002 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0055 | hdong线56杆 | PZXL-00154-N0054 | hdong线56-1杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 3 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0003 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0061 | hdong线61杆 | PZXL-00154-N0062 | hdong线62杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 4 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0004 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0086 | hdong线79-2杆 | PZXL-00154-N0087 | hdong线79-3杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 5 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0005 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0195 | 煤球厂支线02杆 | PZXL-00154-N0196 | 煤球厂支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 6 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0006 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0010 | hdong线14杆 | PZXL-00154-N0011 | hdong线15杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 7 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0007 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0013 | hdong线17杆 | PZXL-00154-N0014 | hdong线18杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 8 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0008 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0178 | 河湾1#支线11杆 | PZXL-00154-N0179 | 河湾1#支线12杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 9 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0009 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0201 | 贝斯卡拉支线001杆 | PZXL-00154-N0202 | 贝斯卡拉支线002杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 10 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0010 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0019 | hdong线22杆 | PZXL-00154-N0020 | hdong线23杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 11 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0011 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0087 | hdong线79-3杆 | PZXL-00154-N0088 | hdong线79-4杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 12 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0012 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0196 | 煤球厂支线03杆 | PZXL-00154-N0197 | 煤球厂支线04杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 13 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0013 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0163 | 日松馆业支线02杆 | PZXL-00154-N0164 | 日松馆业支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 14 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0014 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0011 | hdong线15杆 | PZXL-00154-N0012 | hdong线16杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 15 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0015 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0018 | hdong线21杆 | PZXL-00154-N0019 | hdong线22杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 16 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0016 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0181 | 河湾1#支线14杆 | PZXL-00154-N0182 | 河湾1#支线15杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 17 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0017 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0012 | hdong线16杆 | PZXL-00154-N0013 | hdong线17杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 18 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0018 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0091 | hdong线80杆 | PZXL-00154-N0085 | hdong线79-1杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 19 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0019 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0014 | hdong线18杆 | PZXL-00154-N0015 | hdong线19杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 20 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0020 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0166 | 李口八队电站支线02 | PZXL-00154-N0167 | 李口八队电站支线03 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 21 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0021 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0194 | 煤球厂支线01杆 | PZXL-00154-N0195 | 煤球厂支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 22 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0022 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0005 | hdong线10杆 | PZXL-00154-N0006 | hdong线11杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 23 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0023 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0035 | hdong线37杆 | PZXL-00154-N0036 | hdong线38杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 24 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0024 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0065 | hdong线65杆 | PZXL-00154-N0162 | 日松馆业支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 25 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0025 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0039 | hdong线40杆 | PZXL-00154-N0040 | hdong线41杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 26 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0026 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0069 | hdong线69杆 | PZXL-00154-N0002 | hdong支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 27 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0027 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0065 | hdong线65杆 | PZXL-00154-N0152 | 华运蒜业支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 28 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0028 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0041 | hdong线43杆 | PZXL-00154-N0042 | hdong线44杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 29 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0029 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0023 | hdong线26杆 | PZXL-00154-N0024 | hdong线27杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 30 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0030 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0024 | hdong线27杆 | PZXL-00154-N0025 | hdong线28杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 31 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0031 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0179 | 河湾1#支线12杆 | PZXL-00154-N0180 | 河湾1#支线13杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 32 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0032 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0177 | 河湾1#支线10杆 | PZXL-00154-N0178 | 河湾1#支线11杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 33 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0033 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0176 | 河湾1#支线09杆 | PZXL-00154-N0177 | 河湾1#支线10杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 34 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0034 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0015 | hdong线19杆 | PZXL-00154-N0017 | hdong线20杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 35 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0035 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0009 | hdong线13杆 | PZXL-00154-N0010 | hdong线14杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 36 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0036 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0165 | 李口八队电站支线01 | PZXL-00154-N0166 | 李口八队电站支线02 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 37 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0037 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0021 | hdong线24杆 | PZXL-00154-N0194 | 煤球厂支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 38 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0038 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0114 | hdong线张村2#变支线07杆 | PZXL-00154-N0113 | hdong线张村2#变支线07-1杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 39 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0039 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0162 | 日松馆业支线01杆 | PZXL-00154-N0163 | 日松馆业支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 40 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0040 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0153 | 华运蒜业支线02杆 | PZXL-00154-N0154 | 华运蒜业支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 41 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0041 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0085 | hdong线79-1杆 | PZXL-00154-N0086 | hdong线79-2杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 42 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0042 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0085 | hdong线79-1杆 | PZXL-00154-N0201 | 贝斯卡拉支线001杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 43 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0043 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0078 | hdong线74-04杆 | PZXL-00154-N0079 | hdong线74-05杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 44 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0044 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0087 | hdong线79-3杆 | PZXL-00154-N0200 | 环境卫生管理处支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 45 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0045 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0123 | hdong线张村2#变支线16杆 | PZXL-00154-N0124 | hdong线张村2#变支线17杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 46 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0046 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0026 | hdong线29杆 | PZXL-00154-N0028 | hdong线30杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 47 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0047 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0122 | hdong线张村2#变支线15杆 | PZXL-00154-N0123 | hdong线张村2#变支线16杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 48 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0048 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0134 | hdong线汇龙支线08杆 | PZXL-00154-N0135 | hdong线汇龙支线09杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 49 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0049 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0016 | hdong线1杆 | PZXL-00154-N0027 | hdong线2杆 | 50.0 | JLB3-35 | JLB3-35 (疑似地线/铝包钢类，不应作为10kV相导线瓶颈) | C-PROXY | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 50 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0050 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0038 | hdong线3杆 | PZXL-00154-N0047 | hdong线4杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 51 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0051 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0047 | hdong线4杆 | PZXL-00154-N0059 | hdong线5杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 52 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0052 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0030 | hdong线32杆 | PZXL-00154-N0031 | hdong线33杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 53 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0053 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0029 | hdong线31杆 | PZXL-00154-N0030 | hdong线32杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 54 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0054 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0028 | hdong线30杆 | PZXL-00154-N0029 | hdong线31杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 55 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0055 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0116 | hdong线张村2#变支线09杆 | PZXL-00154-N0117 | hdong线张村2#变支线10杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 56 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0056 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0108 | hdong线张村2#变支线02杆 | PZXL-00154-N0109 | hdong线张村2#变支线03杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 57 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0057 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0059 | hdong线5杆 | PZXL-00154-N0070 | hdong线6杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 58 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0058 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0090 | hdong线7杆 | PZXL-00154-N0101 | hdong线8杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 59 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0059 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0027 | hdong线2杆 | PZXL-00154-N0038 | hdong线3杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 60 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0060 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0125 | hdong线张村2#变支线18杆 | PZXL-00154-N0126 | hdong线张村2#变支线19杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 61 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0061 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0129 | hdong线汇龙支线03杆 | PZXL-00154-N0130 | hdong线汇龙支线04杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 62 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0062 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0111 | hdong线张村2#变支线05杆 | PZXL-00154-N0112 | hdong线张村2#变支线06杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 63 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0063 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0117 | hdong线张村2#变支线10杆 | PZXL-00154-N0118 | hdong线张村2#变支线11杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 64 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0064 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0070 | hdong线6杆 | PZXL-00154-N0090 | hdong线7杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 65 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0065 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0121 | hdong线张村2#变支线14杆 | PZXL-00154-N0122 | hdong线张村2#变支线15杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 66 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0066 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0020 | hdong线23杆 | PZXL-00154-N0127 | hdong线汇龙支线01杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 67 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0067 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0025 | hdong线28杆 | PZXL-00154-N0026 | hdong线29杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 68 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0068 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0110 | hdong线张村2#变支线04杆 | PZXL-00154-N0111 | hdong线张村2#变支线05杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 69 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0069 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0115 | hdong线张村2#变支线08杆 | PZXL-00154-N0116 | hdong线张村2#变支线09杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 70 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0070 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0119 | hdong线张村2#变支线12杆 | PZXL-00154-N0120 | hdong线张村2#变支线13杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 71 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0071 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0128 | hdong线汇龙支线02杆 | PZXL-00154-N0129 | hdong线汇龙支线03杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 72 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0072 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0132 | hdong线汇龙支线06杆 | PZXL-00154-N0133 | hdong线汇龙支线07杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 73 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0073 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0136 | hdong线汇龙支线10杆 | PZXL-00154-N0137 | hdong线汇龙支线11杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 74 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0074 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0069 | hdong线69杆 | PZXL-00154-N0071 | hdong线70杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 75 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0075 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0071 | hdong线70杆 | PZXL-00154-N0072 | hdong线71杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 76 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0076 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0072 | hdong线71杆 | PZXL-00154-N0073 | hdong线72杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 77 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0077 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0065 | hdong线65杆 | PZXL-00154-N0066 | hdong线66杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 78 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0078 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0057 | hdong线58杆 | PZXL-00154-N0058 | hdong线59杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 79 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0079 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0056 | hdong线57杆 | PZXL-00154-N0057 | hdong线58杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 80 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0080 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0052 | hdong线54杆 | PZXL-00154-N0053 | hdong线55杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 81 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0081 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0053 | hdong线55杆 | PZXL-00154-N0055 | hdong线56杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 82 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0082 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0055 | hdong线56杆 | PZXL-00154-N0056 | hdong线57杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 83 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0083 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0051 | hdong线53杆 | PZXL-00154-N0052 | hdong线54杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 84 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0084 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0050 | hdong线52杆 | PZXL-00154-N0051 | hdong线53杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 85 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0085 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0062 | hdong线62杆 | PZXL-00154-N0063 | hdong线63杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 86 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0086 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0063 | hdong线63杆 | PZXL-00154-N0064 | hdong线64杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 87 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0087 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0064 | hdong线64杆 | PZXL-00154-N0065 | hdong线65杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 88 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0088 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0104 | hdong线92杆 | PZXL-00154-N0105 | hdong线93杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 89 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0089 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0092 | hdong线81杆 | PZXL-00154-N0093 | hdong线82杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 90 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0090 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0093 | hdong线82杆 | PZXL-00154-N0094 | hdong线83杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 91 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0091 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0094 | hdong线83杆 | PZXL-00154-N0095 | hdong线84杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 92 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0092 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0095 | hdong线84杆 | PZXL-00154-N0096 | hdong线85杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 93 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0093 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0096 | hdong线85杆 | PZXL-00154-N0097 | hdong线86杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 94 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0094 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0097 | hdong线86杆 | PZXL-00154-N0098 | hdong线87杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 95 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0095 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0084 | hdong线78杆 | PZXL-00154-N0089 | hdong线79杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 96 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0096 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0130 | hdong线汇龙支线04杆 | PZXL-00154-N0131 | hdong线汇龙支线05杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 97 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0097 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0118 | hdong线张村2#变支线11杆 | PZXL-00154-N0119 | hdong线张村2#变支线12杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 98 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0098 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0124 | hdong线张村2#变支线17杆 | PZXL-00154-N0125 | hdong线张村2#变支线18杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 99 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0099 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0133 | hdong线汇龙支线07杆 | PZXL-00154-N0134 | hdong线汇龙支线08杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 100 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0100 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0042 | hdong线44杆 | PZXL-00154-N0043 | hdong线45杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 101 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0101 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0109 | hdong线张村2#变支线03杆 | PZXL-00154-N0110 | hdong线张村2#变支线04杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 102 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0102 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0112 | hdong线张村2#变支线06杆 | PZXL-00154-N0114 | hdong线张村2#变支线07杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 103 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0103 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0022 | hdong线25杆 | PZXL-00154-N0023 | hdong线26杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 104 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0104 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0120 | hdong线张村2#变支线13杆 | PZXL-00154-N0121 | hdong线张村2#变支线14杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 105 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0105 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0101 | hdong线8杆 | PZXL-00154-N0106 | hdong线9杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 106 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0106 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0131 | hdong线汇龙支线05杆 | PZXL-00154-N0132 | hdong线汇龙支线06杆 | 50.0 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | B | 0.1232 | 0.356 | 0.00616 | 0.0178 | 550.0 | 595.22 | 9.5263 | CLOSED | 107 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0107 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0059 | hdong线5杆 | PZXL-00154-N0165 | 李口八队电站支线01 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 108 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0108 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0077 | hdong线74-03杆 | PZXL-00154-N0078 | hdong线74-04杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 109 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0109 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0008 | hdong线12杆 | PZXL-00154-N0009 | hdong线13杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 110 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0110 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0037 | hdong线39杆 | PZXL-00154-N0039 | hdong线40杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 111 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0111 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0073 | hdong线72杆 | PZXL-00154-N0074 | hdong线73杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 112 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0112 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0048 | hdong线50杆 | PZXL-00154-N0049 | hdong线51杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 113 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0113 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0049 | hdong线51杆 | PZXL-00154-N0050 | hdong线52杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 114 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0114 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0060 | hdong线60杆 | PZXL-00154-N0061 | hdong线61杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 115 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0115 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0046 | hdong线49杆 | PZXL-00154-N0048 | hdong线50杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 116 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0116 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0193 | 河镇线hdong48杆 | PZXL-00154-N0046 | hdong线49杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 117 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0117 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0045 | hdong线47杆 | PZXL-00154-N0193 | 河镇线hdong48杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 118 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0118 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0058 | hdong线59杆 | PZXL-00154-N0060 | hdong线60杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 119 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0119 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0148 | 勤丰纺织支线11杆 | PZXL-00154-N0149 | 勤丰纺织支线12杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 120 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0120 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0147 | 勤丰纺织支线10杆 | PZXL-00154-N0148 | 勤丰纺织支线11杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 121 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0121 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0145 | 勤丰纺织支线08杆 | PZXL-00154-N0146 | 勤丰纺织支线09杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 122 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0122 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0146 | 勤丰纺织支线09杆 | PZXL-00154-N0147 | 勤丰纺织支线10杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 123 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0123 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0080 | hdong线74杆 | PZXL-00154-N0138 | 勤丰纺织支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 124 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0124 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0138 | 勤丰纺织支线01杆 | PZXL-00154-N0139 | 勤丰纺织支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 125 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0125 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0139 | 勤丰纺织支线02杆 | PZXL-00154-N0140 | 勤丰纺织支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 126 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0126 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0140 | 勤丰纺织支线03杆 | PZXL-00154-N0141 | 勤丰纺织支线04杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 127 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0127 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0141 | 勤丰纺织支线04杆 | PZXL-00154-N0142 | 勤丰纺织支线05杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 128 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0128 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0089 | hdong线79杆 | PZXL-00154-N0091 | hdong线80杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 129 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0129 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0091 | hdong线80杆 | PZXL-00154-N0092 | hdong线81杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 130 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0130 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0080 | hdong线74杆 | PZXL-00154-N0081 | hdong线75杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 131 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0131 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0192 | 河镇线hdong42杆 | PZXL-00154-N0041 | hdong线43杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 132 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0132 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0081 | hdong线75杆 | PZXL-00154-N0082 | hdong线76杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 133 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0133 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0082 | hdong线76杆 | PZXL-00154-N0083 | hdong线77杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 134 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0134 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0083 | hdong线77杆 | PZXL-00154-N0084 | hdong线78杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 135 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0135 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0182 | 河湾1#支线15杆 | PZXL-00154-N0183 | 河湾1#支线16杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 136 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0136 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0183 | 河湾1#支线16杆 | PZXL-00154-N0184 | 河湾1#支线17杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 137 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0137 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0184 | 河湾1#支线17杆 | PZXL-00154-N0185 | 河湾1#支线18杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 138 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0138 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0185 | 河湾1#支线18杆 | PZXL-00154-N0186 | 河湾1#支线19杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 139 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0139 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0186 | 河湾1#支线19杆 | PZXL-00154-N0187 | 河湾1#支线20杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 140 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0140 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0187 | 河湾1#支线20杆 | PZXL-00154-N0188 | 河湾1#支线21杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 141 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0141 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0188 | 河湾1#支线21杆 | PZXL-00154-N0189 | 河湾1#支线22杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 142 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0142 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0189 | 河湾1#支线22杆 | PZXL-00154-N0190 | 河湾1#支线23杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 143 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0143 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0075 | hdong线74-01杆 | PZXL-00154-N0076 | hdong线74-02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 144 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0144 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0044 | hdong线46杆 | PZXL-00154-N0045 | hdong线47杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 145 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0145 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0021 | hdong线24杆 | PZXL-00154-N0022 | hdong线25杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 146 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0146 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0114 | hdong线张村2#变支线07杆 | PZXL-00154-N0115 | hdong线张村2#变支线08杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 147 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0147 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0017 | hdong线20杆 | PZXL-00154-N0018 | hdong线21杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 148 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0148 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0031 | hdong线33杆 | PZXL-00154-N0032 | hdong线34杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 149 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0149 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0036 | hdong线38杆 | PZXL-00154-N0037 | hdong线39杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 150 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0150 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0033 | hdong线35杆 | PZXL-00154-N0034 | hdong线36杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 151 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0151 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0034 | hdong线36杆 | PZXL-00154-N0035 | hdong线37杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 152 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0152 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0032 | hdong线34杆 | PZXL-00154-N0033 | hdong线35杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 153 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0153 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0066 | hdong线66杆 | PZXL-00154-N0067 | hdong线67杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 154 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0154 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0067 | hdong线67杆 | PZXL-00154-N0068 | hdong线68杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 155 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0155 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0068 | hdong线68杆 | PZXL-00154-N0069 | hdong线69杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 156 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0156 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0142 | 勤丰纺织支线05杆 | PZXL-00154-N0143 | 勤丰纺织支线06杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 157 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0157 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0143 | 勤丰纺织支线06杆 | PZXL-00154-N0144 | 勤丰纺织支线07杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 158 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0158 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0144 | 勤丰纺织支线07杆 | PZXL-00154-N0145 | 勤丰纺织支线08杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 159 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0159 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0192 | 河镇线hdong42杆 | PZXL-00154-N0107 | hdong线张村2#变支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 160 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0160 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0107 | hdong线张村2#变支线01杆 | PZXL-00154-N0108 | hdong线张村2#变支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 161 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0161 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0043 | hdong线45杆 | PZXL-00154-N0044 | hdong线46杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 162 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0162 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0169 | 河湾1#支线02杆 | PZXL-00154-N0170 | 河湾1#支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 163 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0163 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0170 | 河湾1#支线03杆 | PZXL-00154-N0171 | 河湾1#支线04杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 164 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0164 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0171 | 河湾1#支线04杆 | PZXL-00154-N0172 | 河湾1#支线05杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 165 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0165 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0076 | hdong线74-02杆 | PZXL-00154-N0077 | hdong线74-03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 166 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0166 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0141 | 勤丰纺织支线04杆 | PZXL-00154-N0155 | 宏达支01 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 167 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0167 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0152 | 华运蒜业支线01杆 | PZXL-00154-N0153 | 华运蒜业支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 168 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0168 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0080 | hdong线74杆 | PZXL-00154-N0075 | hdong线74-01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 169 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0169 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0100 | hdong线89杆 | PZXL-00154-N0102 | hdong线90杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 170 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0170 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0172 | 河湾1#支线05杆 | PZXL-00154-N0173 | 河湾1#支线06杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 171 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0171 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0173 | 河湾1#支线06杆 | PZXL-00154-N0174 | 河湾1#支线07杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 172 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0172 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0174 | 河湾1#支线07杆 | PZXL-00154-N0175 | 河湾1#支线08杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 173 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0173 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0175 | 河湾1#支线08杆 | PZXL-00154-N0176 | 河湾1#支线09杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 174 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0174 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0149 | 勤丰纺织支线12杆 | PZXL-00154-N0150 | 勤丰纺织支线13杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 175 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0175 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0150 | 勤丰纺织支线13杆 | PZXL-00154-N0151 | 勤丰纺织支线14杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 176 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0176 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0002 | hdong支线01杆 | PZXL-00154-N0003 | hdong支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 177 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0177 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0003 | hdong支线02杆 | PZXL-00154-N0004 | hdong支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 178 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0178 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0002 | hdong支线01杆 | PZXL-00154-N0001 | 3队电站支01 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 179 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0179 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0045 | hdong线47杆 | PZXL-00154-N0191 | 河湾四队电站支01 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 180 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0180 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0168 | 河湾1#支线01杆 | PZXL-00154-N0169 | 河湾1#支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 181 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0181 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0102 | hdong线90杆 | PZXL-00154-N0103 | hdong线91杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 182 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0182 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0103 | hdong线91杆 | PZXL-00154-N0104 | hdong线92杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 183 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0183 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0099 | hdong线88杆 | PZXL-00154-N0100 | hdong线89杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 184 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0184 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0098 | hdong线87杆 | PZXL-00154-N0099 | hdong线88杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 185 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0185 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0180 | 河湾1#支线13杆 | PZXL-00154-N0181 | 河湾1#支线14杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 186 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0186 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0156 | 恒东房地产二支线01杆 | PZXL-00154-N0157 | 恒东房地产二支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 187 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0187 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0159 | 恒东房地产支线01杆 | PZXL-00154-N0160 | 恒东房地产支线02杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 188 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0188 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0112 | hdong线张村2#变支线06杆 | PZXL-00154-N0156 | 恒东房地产二支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 189 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0189 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0198 | 煤球厂支线05杆 | PZXL-00154-N0199 | 煤球厂支线06杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 190 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0190 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0036 | hdong线38杆 | PZXL-00154-N0159 | 恒东房地产支线01杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 191 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0191 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0197 | 煤球厂支线04杆 | PZXL-00154-N0198 | 煤球厂支线05杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 192 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0192 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0160 | 恒东房地产支线02杆 | PZXL-00154-N0161 | 恒东房地产支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 193 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0193 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0157 | 恒东房地产二支线02杆 | PZXL-00154-N0158 | 恒东房地产二支线03杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 194 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0194 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0007 | hdong线12-1 | PZXL-00154-N0008 | hdong线12杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 195 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00154-B0195 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | PZXL-00154-N0135 | hdong线汇龙支线09杆 | PZXL-00154-N0136 | hdong线汇龙支线10杆 | 50.0 | JKLGYJ-240 | JKLGYJ-10-240/30 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 196 | 邳州_10kV河东线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 600 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0001 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0074 | hpao线盛川支线1杆 | PZXL-00161-N0075 | hpao线盛川支线2杆 | 50.0 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 2 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0002 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0065 | hpao线墩既村高坡塑料颗粒产支线06杆 | PZXL-00161-N0066 | hpao线墩既村高坡塑料颗粒产支线07杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 3 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0003 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0032 | hpao线32杆 | PZXL-00161-N0033 | hpao线33杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 4 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0004 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0002 | hpao线02杆 | PZXL-00161-N0003 | hpao线03杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 5 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0005 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0006 | hpao线06杆 | PZXL-00161-N0007 | hpao线07杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 6 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0006 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0016 | hpao线16杆 | PZXL-00161-N0017 | hpao线17杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 7 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0007 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0018 | hpao线18杆 | PZXL-00161-N0019 | hpao线19杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 8 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0008 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0029 | hpao线29杆 | PZXL-00161-N0030 | hpao线30杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 9 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0009 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0005 | hpao线05杆 | PZXL-00161-N0006 | hpao线06杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 10 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0010 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0008 | hpao线08杆 | PZXL-00161-N0009 | hpao线09杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 11 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0011 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0028 | hpao线28杆 | PZXL-00161-N0029 | hpao线29杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 12 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0012 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0023 | hpao线23杆 | PZXL-00161-N0024 | hpao线24杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 13 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0013 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0030 | hpao线30杆 | PZXL-00161-N0031 | hpao线31杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 14 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0014 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0061 | hpao线墩既村高坡塑料颗粒产支线02杆 | PZXL-00161-N0062 | hpao线墩既村高坡塑料颗粒产支线03杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 15 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0015 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0034 | hpao线34杆 | PZXL-00161-N0035 | hpao线35杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 16 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0016 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0040 | hpao线40杆 | PZXL-00161-N0041 | hpao线41杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 17 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0017 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0003 | hpao线03杆 | PZXL-00161-N0004 | hpao线04杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 18 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0018 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0062 | hpao线墩既村高坡塑料颗粒产支线03杆 | PZXL-00161-N0063 | hpao线墩既村高坡塑料颗粒产支线04杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 19 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0019 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0019 | hpao线19杆 | PZXL-00161-N0020 | hpao线20杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 20 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0020 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0033 | hpao线33杆 | PZXL-00161-N0034 | hpao线34杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 21 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0021 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0038 | hpao线38杆 | PZXL-00161-N0039 | hpao线39杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 22 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0022 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0058 | hpao线58杆 | PZXL-00161-N0059 | hpao线59杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 23 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0023 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0057 | hpao线57杆 | PZXL-00161-N0058 | hpao线58杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 24 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0024 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0051 | hpao线51杆 | PZXL-00161-N0052 | hpao线52杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 25 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0025 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0050 | hpao线50杆 | PZXL-00161-N0051 | hpao线51杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 26 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0026 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0052 | hpao线52杆 | PZXL-00161-N0053 | hpao线53杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 27 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0027 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0056 | hpao线56杆 | PZXL-00161-N0057 | hpao线57杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 28 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0028 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0049 | hpao线49杆 | PZXL-00161-N0050 | hpao线50杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 29 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0029 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0055 | hpao线55杆 | PZXL-00161-N0056 | hpao线56杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 30 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0030 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0053 | hpao线53杆 | PZXL-00161-N0054 | hpao线54杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 31 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0031 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0060 | hpao线墩既村高坡塑料颗粒产支线01杆 | PZXL-00161-N0061 | hpao线墩既村高坡塑料颗粒产支线02杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 32 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0032 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0009 | hpao线09杆 | PZXL-00161-N0010 | hpao线10杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 33 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0033 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0035 | hpao线35杆 | PZXL-00161-N0036 | hpao线36杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 34 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0034 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0037 | hpao线37杆 | PZXL-00161-N0038 | hpao线38杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 35 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0035 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0014 | hpao线14杆 | PZXL-00161-N0015 | hpao线15杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 36 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0036 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0013 | hpao线13杆 | PZXL-00161-N0014 | hpao线14杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 37 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0037 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0048 | hpao线48杆 | PZXL-00161-N0049 | hpao线49杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 38 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0038 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0047 | hpao线47杆 | PZXL-00161-N0048 | hpao线48杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 39 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0039 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0044 | hpao线44杆 | PZXL-00161-N0045 | hpao线45杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 40 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0040 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0046 | hpao线46杆 | PZXL-00161-N0047 | hpao线47杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 41 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0041 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0045 | hpao线45杆 | PZXL-00161-N0046 | hpao线46杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 42 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0042 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0054 | hpao线54杆 | PZXL-00161-N0055 | hpao线55杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 43 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0043 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0015 | hpao线15杆 | PZXL-00161-N0016 | hpao线16杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 44 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0044 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0021 | hpao线21杆 | PZXL-00161-N0022 | hpao线22杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 45 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0045 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0022 | hpao线22杆 | PZXL-00161-N0023 | hpao线23杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 46 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0046 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0031 | hpao线31杆 | PZXL-00161-N0032 | hpao线32杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 47 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0047 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0011 | hpao线11杆 | PZXL-00161-N0012 | hpao线12杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 48 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0048 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0027 | hpao线27杆 | PZXL-00161-N0028 | hpao线28杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 49 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0049 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0007 | hpao线07杆 | PZXL-00161-N0008 | hpao线08杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 50 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0050 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0026 | hpao线26杆 | PZXL-00161-N0027 | hpao线27杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 51 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0051 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0004 | hpao线04杆 | PZXL-00161-N0005 | hpao线05杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 52 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0052 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0064 | hpao线墩既村高坡塑料颗粒产支线05杆 | PZXL-00161-N0065 | hpao线墩既村高坡塑料颗粒产支线06杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 53 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0053 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0024 | hpao线24杆 | PZXL-00161-N0025 | hpao线25杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 54 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0054 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0039 | hpao线39杆 | PZXL-00161-N0040 | hpao线40杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 55 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0055 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0001 | hpao线01杆 | PZXL-00161-N0002 | hpao线02杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 56 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0056 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0020 | hpao线20杆 | PZXL-00161-N0021 | hpao线21杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 57 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0057 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0041 | hpao线41杆 | PZXL-00161-N0042 | hpao线42杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 58 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0058 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0017 | hpao线17杆 | PZXL-00161-N0018 | hpao线18杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 59 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0059 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0025 | hpao线25杆 | PZXL-00161-N0026 | hpao线26杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 60 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0060 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0010 | hpao线10杆 | PZXL-00161-N0011 | hpao线11杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 61 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0061 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0012 | hpao线12杆 | PZXL-00161-N0013 | hpao线13杆 | 50.0 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 62 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0062 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0063 | hpao线墩既村高坡塑料颗粒产支线04杆 | PZXL-00161-N0064 | hpao线墩既村高坡塑料颗粒产支线05杆 | 50.0 | JKLYJ-150 | JKLYJ-10-150 | A/B | 0.26368 | 0.295839341 | 0.013184 | 0.01479197 | 285.0 | 400.0 | 4.9363 | CLOSED | 63 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 285 | 4.9363 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0063 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0077 | hpao线盛川支线4杆 | PZXL-00161-N0078 | hpao线盛川支线5杆 | 50.0 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 64 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0064 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0052 | hpao线52杆 | PZXL-00161-N0074 | hpao线盛川支线1杆 | 50.0 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 65 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0065 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0075 | hpao线盛川支线2杆 | PZXL-00161-N0076 | hpao线盛川支线3杆 | 50.0 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 66 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0066 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0076 | hpao线盛川支线3杆 | PZXL-00161-N0077 | hpao线盛川支线4杆 | 50.0 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | B | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 67 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0067 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0072 | hpao线王场湖支线1杆 | PZXL-00161-N0073 | hpao线王场湖支线2杆 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 68 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0068 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0067 | hpao线墩既村高坡塑料颗粒产支线10 | PZXL-00161-N0068 | hpao线墩既村高坡塑料颗粒产支线11 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 69 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0069 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0070 | hpao线墩既村高坡塑料颗粒产支线9 | PZXL-00161-N0067 | hpao线墩既村高坡塑料颗粒产支线10 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 70 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0070 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0043 | hpao线43杆 | PZXL-00161-N0071 | hpao线王场湖排灌站支线1杆 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 71 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0071 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0069 | hpao线墩既村高坡塑料颗粒产支线8 | PZXL-00161-N0070 | hpao线墩既村高坡塑料颗粒产支线9 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 72 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00161-B0072 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | PZXL-00161-N0066 | hpao线墩既村高坡塑料颗粒产支线07杆 | PZXL-00161-N0069 | hpao线墩既村高坡塑料颗粒产支线8 | 50.0 | JL/G1A-240/30 | JL/G1A-240/30 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 550.0 | 562.0 | 9.5263 | CLOSED | 73 | 邳州_10kV河炮线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 595 | 550 | 9.5263 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0001 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0054 | 10kVhzhen线56#杆 | PZXL-00173-N0099 | hzhen线56-1 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 2 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0002 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0190 | 张村1变支线33杆 | PZXL-00173-N0191 | 张村1变支线34杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 3 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0003 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0192 | 张村1变支线35杆 | PZXL-00173-N0193 | 张村1变支线36杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 4 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0004 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0189 | 张村1变支线32杆 | PZXL-00173-N0190 | 张村1变支线33杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 5 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0005 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0193 | 张村1变支线36杆 | PZXL-00173-N0194 | 张村1变支线37杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 6 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0006 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0191 | 张村1变支线34杆 | PZXL-00173-N0192 | 张村1变支线35杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 7 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0007 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0194 | 张村1变支线37杆 | PZXL-00173-N0195 | 张村1变支线38杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 8 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0008 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | PZXL-00173-N0002 | 10kVhzhen线02#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 9 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0009 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0059 | 10kVhzhen线61#杆 | PZXL-00173-N0060 | 10kVhzhen线62#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 10 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0010 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0126 | 南方永磁支线8杆 | PZXL-00173-N0127 | 南方永磁支线9杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 11 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0011 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0111 | 南方永磁支线12杆 | PZXL-00173-N0112 | 南方永磁支线13杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 12 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0012 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0117 | 南方永磁支线18杆 | PZXL-00173-N0118 | 南方永磁支线19杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 13 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0013 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0122 | 南方永磁支线4杆 | PZXL-00173-N0123 | 南方永磁支线5杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 14 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0014 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0114 | 南方永磁支线15杆 | PZXL-00173-N0115 | 南方永磁支线16杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 15 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0015 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0115 | 南方永磁支线16杆 | PZXL-00173-N0116 | 南方永磁支线17杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 16 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0016 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0110 | 南方永磁支线11杆 | PZXL-00173-N0111 | 南方永磁支线12杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 17 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0017 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0127 | 南方永磁支线9杆 | PZXL-00173-N0109 | 南方永磁支线10杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 18 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0018 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0125 | 南方永磁支线7杆 | PZXL-00173-N0126 | 南方永磁支线8杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 19 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0019 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0120 | 南方永磁支线2杆 | PZXL-00173-N0121 | 南方永磁支线3杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 20 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0020 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0123 | 南方永磁支线5杆 | PZXL-00173-N0124 | 南方永磁支线6杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 21 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0021 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0096 | 10kVhzhen线93杆 | PZXL-00173-N0119 | 南方永磁支线1杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 22 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0022 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0116 | 南方永磁支线17杆 | PZXL-00173-N0117 | 南方永磁支线18杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 23 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0023 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0124 | 南方永磁支线6杆 | PZXL-00173-N0125 | 南方永磁支线7杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 24 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0024 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0121 | 南方永磁支线3杆 | PZXL-00173-N0122 | 南方永磁支线4杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 25 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0025 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0113 | 南方永磁支线14杆 | PZXL-00173-N0114 | 南方永磁支线15杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 26 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0026 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0112 | 南方永磁支线13杆 | PZXL-00173-N0113 | 南方永磁支线14杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 27 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0027 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0109 | 南方永磁支线10杆 | PZXL-00173-N0110 | 南方永磁支线11杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 28 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0028 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0119 | 南方永磁支线1杆 | PZXL-00173-N0120 | 南方永磁支线2杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 29 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0029 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0213 | 文苑路支线26杆 | PZXL-00173-N0214 | 文苑路支线27杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 30 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0030 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0208 | 文苑路支线21杆 | PZXL-00173-N0209 | 文苑路支线22杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 31 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0031 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0211 | 文苑路支线24杆 | PZXL-00173-N0212 | 文苑路支线25杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 32 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0032 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0224 | 文苑路支线8杆 | PZXL-00173-N0225 | 文苑路支线9杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 33 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0033 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0206 | 文苑路支线1杆 | PZXL-00173-N0217 | 文苑路支线2杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 34 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0034 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0221 | 文苑路支线5杆 | PZXL-00173-N0222 | 文苑路支线6杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 35 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0035 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0197 | 文苑路支线11杆 | PZXL-00173-N0198 | 文苑路支线12杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 36 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0036 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0196 | 文苑路支线10杆 | PZXL-00173-N0197 | 文苑路支线11杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 37 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0037 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0210 | 文苑路支线23杆 | PZXL-00173-N0211 | 文苑路支线24杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 38 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0038 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0222 | 文苑路支线6杆 | PZXL-00173-N0223 | 文苑路支线7杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 39 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0039 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0223 | 文苑路支线7杆 | PZXL-00173-N0224 | 文苑路支线8杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 40 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0040 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0204 | 文苑路支线18杆 | PZXL-00173-N0205 | 文苑路支线19杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 41 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0041 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0217 | 文苑路支线2杆 | PZXL-00173-N0219 | 文苑路支线3杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 42 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0042 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0207 | 文苑路支线20杆 | PZXL-00173-N0208 | 文苑路支线21杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 43 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0043 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0220 | 文苑路支线4杆 | PZXL-00173-N0221 | 文苑路支线5杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 44 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0044 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0202 | 文苑路支线16杆 | PZXL-00173-N0203 | 文苑路支线17杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 45 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0045 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0199 | 文苑路支线13杆 | PZXL-00173-N0200 | 文苑路支线14杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 46 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0046 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0225 | 文苑路支线9杆 | PZXL-00173-N0196 | 文苑路支线10杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 47 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0047 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0200 | 文苑路支线14杆 | PZXL-00173-N0201 | 文苑路支线15杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 48 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0048 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0209 | 文苑路支线22杆 | PZXL-00173-N0210 | 文苑路支线23杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 49 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0049 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0219 | 文苑路支线3杆 | PZXL-00173-N0220 | 文苑路支线4杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 50 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0050 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0047 | 10kVhzhen线49#杆 | PZXL-00173-N0206 | 文苑路支线1杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 51 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0051 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0216 | 文苑路支线29杆 | PZXL-00173-N0218 | 文苑路支线30杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 52 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0052 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0205 | 文苑路支线19杆 | PZXL-00173-N0207 | 文苑路支线20杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 53 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0053 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0203 | 文苑路支线17杆 | PZXL-00173-N0204 | 文苑路支线18杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 54 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0054 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0214 | 文苑路支线27杆 | PZXL-00173-N0215 | 文苑路支线28杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 55 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0055 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0212 | 文苑路支线25杆 | PZXL-00173-N0213 | 文苑路支线26杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 56 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0056 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0215 | 文苑路支线28杆 | PZXL-00173-N0216 | 文苑路支线29杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 57 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0057 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0198 | 文苑路支线12杆 | PZXL-00173-N0199 | 文苑路支线13杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 58 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0058 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0201 | 文苑路支线15杆 | PZXL-00173-N0202 | 文苑路支线16杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 59 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0059 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0039 | 10kVhzhen线40#杆 | PZXL-00173-N0132 | 工业园区支线01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 60 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0060 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0036 | 10kVhzhen线37#杆 | PZXL-00173-N0037 | 10kVhzhen线38#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 61 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0061 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0143 | 工业园区支线12杆 | PZXL-00173-N0144 | 工业园区支线13杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 62 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0062 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0005 | 10kVhzhen线05#杆 | PZXL-00173-N0006 | 10kVhzhen线06#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 63 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0063 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0146 | 工业园区支线15杆 | PZXL-00173-N0147 | 工业园区支线16杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 64 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0064 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0132 | 工业园区支线01杆 | PZXL-00173-N0133 | 工业园区支线02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 65 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0065 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0046 | 10kVhzhen线48#杆 | PZXL-00173-N0047 | 10kVhzhen线49#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 66 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0066 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0012 | 10kVhzhen线13#杆 | PZXL-00173-N0013 | 10kVhzhen线14#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 67 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0067 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0135 | 工业园区支线04杆 | PZXL-00173-N0136 | 工业园区支线05杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 68 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0068 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0010 | 10kVhzhen线11#杆 | PZXL-00173-N0011 | 10kVhzhen线12#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 69 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0069 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0011 | 10kVhzhen线12#杆 | PZXL-00173-N0012 | 10kVhzhen线13#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 70 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0070 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0154 | 张村10变支线05杆 | PZXL-00173-N0155 | 张村10变支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 71 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0071 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0155 | 张村10变支线06杆 | PZXL-00173-N0156 | 张村10变支线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 72 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0072 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0156 | 张村10变支线07杆 | PZXL-00173-N0157 | 张村10变支线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 73 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0073 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0187 | 张村1变支线30杆 | PZXL-00173-N0188 | 张村1变支线31杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 74 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0074 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0186 | 张村1变支线29杆 | PZXL-00173-N0187 | 张村1变支线30杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 75 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0075 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0188 | 张村1变支线31杆 | PZXL-00173-N0189 | 张村1变支线32杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 76 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0076 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0072 | 10kVhzhen线74杆 | PZXL-00173-N0078 | 10kVhzhen线75杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 77 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0077 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0078 | 10kVhzhen线75杆 | PZXL-00173-N0079 | 10kVhzhen线76杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 78 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0078 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0138 | 工业园区支线07杆 | PZXL-00173-N0139 | 工业园区支线08杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 79 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0079 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0185 | 张村1变支线28杆 | PZXL-00173-N0186 | 张村1变支线29杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 80 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0080 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0171 | 张村1变支线14杆 | PZXL-00173-N0240 | 运河张村11变支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 81 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0081 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0180 | 张村1变支线23杆 | PZXL-00173-N0181 | 张村1变支线24杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 82 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0082 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0153 | 张村10变支线04杆 | PZXL-00173-N0154 | 张村10变支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 83 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0083 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0171 | 张村1变支线14杆 | PZXL-00173-N0172 | 张村1变支线15杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 84 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0084 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0183 | 张村1变支线26杆 | PZXL-00173-N0184 | 张村1变支线27杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 85 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0085 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0152 | 张村10变支线03杆 | PZXL-00173-N0153 | 张村10变支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 86 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0086 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0177 | 张村1变支线20杆 | PZXL-00173-N0150 | 张村10变支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 87 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0087 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0173 | 张村1变支线16杆 | PZXL-00173-N0174 | 张村1变支线17杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 88 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0088 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0150 | 张村10变支线01杆 | PZXL-00173-N0151 | 张村10变支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 89 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0089 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0176 | 张村1变支线19杆 | PZXL-00173-N0177 | 张村1变支线20杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 90 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0090 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0174 | 张村1变支线17杆 | PZXL-00173-N0175 | 张村1变支线18杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 91 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0091 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0175 | 张村1变支线18杆 | PZXL-00173-N0176 | 张村1变支线19杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 92 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0092 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0172 | 张村1变支线15杆 | PZXL-00173-N0173 | 张村1变支线16杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 93 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0093 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0177 | 张村1变支线20杆 | PZXL-00173-N0178 | 张村1变支线21杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 94 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0094 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0158 | 张村1变支线01杆 | PZXL-00173-N0159 | 张村1变支线02杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 95 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0095 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0160 | 张村1变支线03杆 | PZXL-00173-N0161 | 张村1变支线04杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 96 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0096 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0161 | 张村1变支线04杆 | PZXL-00173-N0162 | 张村1变支线05杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 97 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0097 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0162 | 张村1变支线05杆 | PZXL-00173-N0163 | 张村1变支线06杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 98 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0098 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0163 | 张村1变支线06杆 | PZXL-00173-N0164 | 张村1变支线07杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 99 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0099 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0165 | 张村1变支线08杆 | PZXL-00173-N0166 | 张村1变支线09杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 100 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0100 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0166 | 张村1变支线09杆 | PZXL-00173-N0167 | 张村1变支线10杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 101 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0101 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0151 | 张村10变支线02杆 | PZXL-00173-N0152 | 张村10变支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 102 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0102 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0178 | 张村1变支线21杆 | PZXL-00173-N0179 | 张村1变支线22杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 103 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0103 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0179 | 张村1变支线22杆 | PZXL-00173-N0180 | 张村1变支线23杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 104 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0104 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0181 | 张村1变支线24杆 | PZXL-00173-N0182 | 张村1变支线25杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 105 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0105 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0182 | 张村1变支线25杆 | PZXL-00173-N0183 | 张村1变支线26杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 106 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0106 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0184 | 张村1变支线27杆 | PZXL-00173-N0185 | 张村1变支线28杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 107 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0107 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0167 | 张村1变支线10杆 | PZXL-00173-N0168 | 张村1变支线11杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 108 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0108 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0168 | 张村1变支线11杆 | PZXL-00173-N0169 | 张村1变支线12杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 109 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0109 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0169 | 张村1变支线12杆 | PZXL-00173-N0170 | 张村1变支线13杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 110 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0110 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0170 | 张村1变支线13杆 | PZXL-00173-N0171 | 张村1变支线14杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 111 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0111 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0164 | 张村1变支线07杆 | PZXL-00173-N0165 | 张村1变支线08杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 112 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0112 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0086 | 10kVhzhen线83杆 | PZXL-00173-N0158 | 张村1变支线01杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 113 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0113 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0159 | 张村1变支线02杆 | PZXL-00173-N0160 | 张村1变支线03杆 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 114 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0114 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0161 | 张村1变支线04杆 | PZXL-00173-N0229 | 河湾4＃变支01 | 50.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0065 | 0.0178 | 500.0 | 550.0 | 8.6603 | CLOSED | 115 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0115 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PZXL-00173-N0230 | 看守所支线01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 116 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0116 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0236 | 看守所支线07杆 | PZXL-00173-N0237 | 看守所支线08杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 117 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0117 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0042 | 10kVhzhen线43#杆 | PZXL-00173-N0043 | 10kVhzhen线44#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 118 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0118 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0045 | 10kVhzhen线47#杆 | PZXL-00173-N0046 | 10kVhzhen线48#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 119 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0119 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0235 | 看守所支线06杆 | PZXL-00173-N0236 | 看守所支线07杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 120 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0120 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0027 | 10kVhzhen线28#杆 | PZXL-00173-N0028 | 10kVhzhen线29#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 121 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0121 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0147 | 工业园区支线16杆 | PZXL-00173-N0148 | 工业园区支线17杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 122 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0122 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0033 | 10kVhzhen线34#杆 | PZXL-00173-N0034 | 10kVhzhen线35#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 123 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0123 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0044 | 10kVhzhen线46#杆 | PZXL-00173-N0045 | 10kVhzhen线47#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 124 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0124 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0015 | 10kVhzhen线16#杆 | PZXL-00173-N0016 | 10kVhzhen线17#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 125 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0125 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0026 | 10kVhzhen线27#杆 | PZXL-00173-N0027 | 10kVhzhen线28#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 126 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0126 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0028 | 10kVhzhen线29#杆 | PZXL-00173-N0029 | 10kVhzhen线30#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 127 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0127 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0098 | hzhen线45杆 | PZXL-00173-N0044 | 10kVhzhen线46#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 128 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0128 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0232 | 看守所支线03杆 | PZXL-00173-N0233 | 看守所支线04杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 129 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0129 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0041 | 10kVhzhen线42#杆 | PZXL-00173-N0042 | 10kVhzhen线43#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 130 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0130 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0134 | 工业园区支线03杆 | PZXL-00173-N0226 | 欢乐买支线01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 131 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0131 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0017 | 10kVhzhen线18#杆 | PZXL-00173-N0018 | 10kVhzhen线19#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 132 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0132 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0022 | 10kVhzhen线23#杆 | PZXL-00173-N0023 | 10kVhzhen线24#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 133 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0133 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PZXL-00173-N0021 | 10kVhzhen线22#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 134 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0134 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0141 | 工业园区支线10杆 | PZXL-00173-N0142 | 工业园区支线11杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 135 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0135 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0019 | 10kVhzhen线20#杆 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 136 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0136 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0038 | 10kVhzhen线39#杆 | PZXL-00173-N0039 | 10kVhzhen线40#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 137 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0137 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0234 | 看守所支线05杆 | PZXL-00173-N0235 | 看守所支线06杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 138 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0138 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0014 | 10kVhzhen线15#杆 | PZXL-00173-N0015 | 10kVhzhen线16#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 139 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0139 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0016 | 10kVhzhen线17#杆 | PZXL-00173-N0017 | 10kVhzhen线18#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 140 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0140 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0025 | 10kVhzhen线26#杆 | PZXL-00173-N0026 | 10kVhzhen线27#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 141 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0141 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0133 | 工业园区支线02杆 | PZXL-00173-N0134 | 工业园区支线03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 142 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0142 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0040 | 10kVhzhen线41#杆 | PZXL-00173-N0041 | 10kVhzhen线42#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 143 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0143 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0134 | 工业园区支线03杆 | PZXL-00173-N0135 | 工业园区支线04杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 144 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0144 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0226 | 欢乐买支线01杆 | PZXL-00173-N0227 | 欢乐买支线02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 145 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0145 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0013 | 10kVhzhen线14#杆 | PZXL-00173-N0014 | 10kVhzhen线15#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 146 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0146 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0030 | 10kVhzhen线31#杆 | PZXL-00173-N0031 | 10kVhzhen线32#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 147 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0147 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0024 | 10kVhzhen线25#杆 | PZXL-00173-N0025 | 10kVhzhen线26#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 148 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0148 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0003 | 10kVhzhen线03#杆 | PZXL-00173-N0004 | 10kVhzhen线04#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 149 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0149 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0006 | 10kVhzhen线06#杆 | PZXL-00173-N0097 | hzhen线07杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 150 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0150 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0148 | 工业园区支线17杆 | PZXL-00173-N0149 | 工业园区支线18杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 151 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0151 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0137 | 工业园区支线06杆 | PZXL-00173-N0138 | 工业园区支线07杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 152 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0152 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0002 | 10kVhzhen线02#杆 | PZXL-00173-N0003 | 10kVhzhen线03#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 153 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0153 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0007 | 10kVhzhen线08#杆 | PZXL-00173-N0008 | 10kVhzhen线09#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 154 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0154 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0140 | 工业园区支线09杆 | PZXL-00173-N0141 | 工业园区支线10杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 155 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0155 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0037 | 10kVhzhen线38#杆 | PZXL-00173-N0038 | 10kVhzhen线39#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 156 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0156 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0004 | 10kVhzhen线04#杆 | PZXL-00173-N0005 | 10kVhzhen线05#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 157 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0157 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0144 | 工业园区支线13杆 | PZXL-00173-N0145 | 工业园区支线14杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 158 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0158 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0018 | 10kVhzhen线19#杆 | PZXL-00173-N0019 | 10kVhzhen线20#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 159 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0159 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0029 | 10kVhzhen线30#杆 | PZXL-00173-N0030 | 10kVhzhen线31#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 160 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0160 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0008 | 10kVhzhen线09#杆 | PZXL-00173-N0009 | 10kVhzhen线10#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 161 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0161 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0021 | 10kVhzhen线22#杆 | PZXL-00173-N0022 | 10kVhzhen线23#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 162 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0162 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0032 | 10kVhzhen线33#杆 | PZXL-00173-N0033 | 10kVhzhen线34#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 163 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0163 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0034 | 10kVhzhen线35#杆 | PZXL-00173-N0035 | 10kVhzhen线36#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 164 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0164 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0009 | 10kVhzhen线10#杆 | PZXL-00173-N0010 | 10kVhzhen线11#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 165 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0165 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0145 | 工业园区支线14杆 | PZXL-00173-N0146 | 工业园区支线15杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 166 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0166 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0233 | 看守所支线04杆 | PZXL-00173-N0234 | 看守所支线05杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 167 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0167 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0035 | 10kVhzhen线36#杆 | PZXL-00173-N0036 | 10kVhzhen线37#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 168 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0168 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0097 | hzhen线07杆 | PZXL-00173-N0007 | 10kVhzhen线08#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 169 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0169 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0039 | 10kVhzhen线40#杆 | PZXL-00173-N0040 | 10kVhzhen线41#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 170 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0170 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0142 | 工业园区支线11杆 | PZXL-00173-N0143 | 工业园区支线12杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 171 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0171 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0139 | 工业园区支线08杆 | PZXL-00173-N0140 | 工业园区支线09杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 172 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0172 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0023 | 10kVhzhen线24#杆 | PZXL-00173-N0024 | 10kVhzhen线25#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 173 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0173 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0043 | 10kVhzhen线44#杆 | PZXL-00173-N0098 | hzhen线45杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 174 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0174 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0031 | 10kVhzhen线32#杆 | PZXL-00173-N0032 | 10kVhzhen线33#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 175 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0175 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0231 | 看守所支线02杆 | PZXL-00173-N0232 | 看守所支线03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 176 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0176 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0106 | hzhen线勤丰纺织支线07杆 | PZXL-00173-N0107 | hzhen线勤丰纺织支线08杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 177 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0177 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0056 | 10kVhzhen线58#杆 | PZXL-00173-N0057 | 10kVhzhen线59#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 178 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0178 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0068 | 10kVhzhen线70#杆 | PZXL-00173-N0069 | 10kVhzhen线71#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 179 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0179 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0234 | 看守所支线05杆 | PZXL-00173-N0238 | 看守所支线3-01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 180 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0180 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0073 | 10kVhzhen线75-01杆 | PZXL-00173-N0074 | 10kVhzhen线75-02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 181 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0181 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0227 | 欢乐买支线02杆 | PZXL-00173-N0228 | 欢乐买支线03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 182 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0182 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0082 | 10kVhzhen线79杆 | PZXL-00173-N0128 | 垃圾站支线01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 183 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0183 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0230 | 看守所支线01杆 | PZXL-00173-N0231 | 看守所支线02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 184 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0184 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0051 | 10kVhzhen线53#杆 | PZXL-00173-N0052 | 10kVhzhen线54#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 185 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0185 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0055 | 10kVhzhen线57#杆 | PZXL-00173-N0056 | 10kVhzhen线58#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 186 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0186 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0054 | 10kVhzhen线56#杆 | PZXL-00173-N0055 | 10kVhzhen线57#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 187 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0187 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0128 | 垃圾站支线01杆 | PZXL-00173-N0129 | 垃圾站支线02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 188 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0188 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0104 | hzhen线勤丰纺织支线05杆 | PZXL-00173-N0105 | hzhen线勤丰纺织支线06杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 189 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0189 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0052 | 10kVhzhen线54#杆 | PZXL-00173-N0053 | 10kVhzhen线55#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 190 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0190 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0075 | 10kVhzhen线75-03杆 | PZXL-00173-N0076 | 10kVhzhen线75-04杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 191 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0191 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0084 | 10kVhzhen线81杆 | PZXL-00173-N0085 | 10kVhzhen线82杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 192 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0192 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0083 | 10kVhzhen线80杆 | PZXL-00173-N0084 | 10kVhzhen线81杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 193 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0193 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0107 | hzhen线勤丰纺织支线08杆 | PZXL-00173-N0108 | hzhen线勤丰纺织支线09杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 194 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0194 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0069 | 10kVhzhen线71#杆 | PZXL-00173-N0070 | 10kVhzhen线72#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 195 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0195 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0057 | 10kVhzhen线59#杆 | PZXL-00173-N0058 | 10kVhzhen线60#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 196 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0196 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0094 | 10kVhzhen线91杆 | PZXL-00173-N0095 | 10kVhzhen线92杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 197 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0197 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0105 | hzhen线勤丰纺织支线06杆 | PZXL-00173-N0106 | hzhen线勤丰纺织支线07杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 198 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0198 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0048 | 10kVhzhen线50#杆 | PZXL-00173-N0049 | 10kVhzhen线51#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 199 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0199 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0078 | 10kVhzhen线75杆 | PZXL-00173-N0100 | hzhen线勤丰纺织支线01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 200 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0200 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0092 | 10kVhzhen线89杆 | PZXL-00173-N0093 | 10kVhzhen线90杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 201 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0201 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0076 | 10kVhzhen线75-04杆 | PZXL-00173-N0077 | 10kVhzhen线75-05杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 202 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0202 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0100 | hzhen线勤丰纺织支线01杆 | PZXL-00173-N0101 | hzhen线勤丰纺织支线02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 203 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0203 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0060 | 10kVhzhen线62#杆 | PZXL-00173-N0061 | 10kVhzhen线63#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 204 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0204 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0070 | 10kVhzhen线72#杆 | PZXL-00173-N0071 | 10kVhzhen线73#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 205 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0205 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0090 | 10kVhzhen线87杆 | PZXL-00173-N0091 | 10kVhzhen线88杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 206 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0206 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0089 | 10kVhzhen线86杆 | PZXL-00173-N0090 | 10kVhzhen线87杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 207 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0207 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0047 | 10kVhzhen线49#杆 | PZXL-00173-N0048 | 10kVhzhen线50#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 208 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0208 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0049 | 10kVhzhen线51#杆 | PZXL-00173-N0050 | 10kVhzhen线52#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 209 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0209 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0087 | 10kVhzhen线84杆 | PZXL-00173-N0088 | 10kVhzhen线85杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 210 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0210 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0238 | 看守所支线3-01杆 | PZXL-00173-N0239 | 看守所支线3-02杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 211 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0211 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0129 | 垃圾站支线02杆 | PZXL-00173-N0130 | 垃圾站支线03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 212 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0212 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0102 | hzhen线勤丰纺织支线03杆 | PZXL-00173-N0103 | hzhen线勤丰纺织支线04杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 213 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0213 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0066 | 10kVhzhen线68#杆 | PZXL-00173-N0067 | 10kVhzhen线69#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 214 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0214 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0088 | 10kVhzhen线85杆 | PZXL-00173-N0089 | 10kVhzhen线86杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 215 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0215 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0080 | 10kVhzhen线77杆 | PZXL-00173-N0081 | 10kVhzhen线78杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 216 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0216 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0074 | 10kVhzhen线75-02杆 | PZXL-00173-N0075 | 10kVhzhen线75-03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 217 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0217 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0081 | 10kVhzhen线78杆 | PZXL-00173-N0082 | 10kVhzhen线79杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 218 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0218 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0085 | 10kVhzhen线82杆 | PZXL-00173-N0086 | 10kVhzhen线83杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 219 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0219 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0050 | 10kVhzhen线52#杆 | PZXL-00173-N0051 | 10kVhzhen线53#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 220 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0220 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0095 | 10kVhzhen线92杆 | PZXL-00173-N0096 | 10kVhzhen线93杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 221 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0221 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0062 | 10kVhzhen线64#杆 | PZXL-00173-N0063 | 10kVhzhen线65#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 222 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0222 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0058 | 10kVhzhen线60#杆 | PZXL-00173-N0059 | 10kVhzhen线61#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 223 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0223 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0101 | hzhen线勤丰纺织支线02杆 | PZXL-00173-N0102 | hzhen线勤丰纺织支线03杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 224 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0224 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0086 | 10kVhzhen线83杆 | PZXL-00173-N0087 | 10kVhzhen线84杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 225 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0225 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0053 | 10kVhzhen线55#杆 | PZXL-00173-N0054 | 10kVhzhen线56#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 226 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0226 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0082 | 10kVhzhen线79杆 | PZXL-00173-N0083 | 10kVhzhen线80杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 227 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0227 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0065 | 10kVhzhen线67#杆 | PZXL-00173-N0066 | 10kVhzhen线68#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 228 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0228 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0079 | 10kVhzhen线76杆 | PZXL-00173-N0080 | 10kVhzhen线77杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 229 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0229 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0130 | 垃圾站支线03杆 | PZXL-00173-N0131 | 垃圾站支线04杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 230 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0230 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0067 | 10kVhzhen线69#杆 | PZXL-00173-N0068 | 10kVhzhen线70#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 231 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0231 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0093 | 10kVhzhen线90杆 | PZXL-00173-N0094 | 10kVhzhen线91杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 232 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0232 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0103 | hzhen线勤丰纺织支线04杆 | PZXL-00173-N0104 | hzhen线勤丰纺织支线05杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 233 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0233 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0061 | 10kVhzhen线63#杆 | PZXL-00173-N0062 | 10kVhzhen线64#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 234 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0234 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0063 | 10kVhzhen线65#杆 | PZXL-00173-N0064 | 10kVhzhen线66#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 235 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0235 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0091 | 10kVhzhen线88杆 | PZXL-00173-N0092 | 10kVhzhen线89杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 236 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0236 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0064 | 10kVhzhen线66#杆 | PZXL-00173-N0065 | 10kVhzhen线67#杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 237 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0237 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0078 | 10kVhzhen线75杆 | PZXL-00173-N0073 | 10kVhzhen线75-01杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 238 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)
PZXL-00173-B0238 | PHYSICAL_SPAN | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | PZXL-00173-N0136 | 工业园区支线05杆 | PZXL-00173-N0137 | 工业园区支线06杆 | 60.0 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | B+ | 0.13 | 0.356 | 0.0078 | 0.02136 | 500.0 | 550.0 | 8.6603 | CLOSED | 239 | 邳州_10kV河镇线明细.xlsx | PARAMETERIZED_PLANNING_MODEL | 605 | 500 | 8.6603 | min(conductor_Imax_base, SRC06_feeder_max_allowed_current)

## 16_switch_master
switch_id | repair_id | station_id | station_name | feeder_id | feeder_alias | switch_name | from_node_name | from_node_id | to_node_name | to_node_id | device_type | confirmed_structure | normal_state | debug_state | remote_control | length_m | r_ohm | x_ohm | evidence | confidence | allow_debug_autofix | blocking_final | resolution
PZXL-00099-SW-R004 | R004 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | dzhen线07开关 | dzhen线07杆 | PZXL-00099-N0007 | dzhen线08杆 | PZXL-00099-N0008 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认开关设备导致结构化表断边 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00097-SW-R009 | R009 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线24开关 | dxi线23杆 | PZXL-00097-N0067 | dxi线24杆 | PZXL-00097-N0068 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认23/24之间存在开关 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00154-SW-R013 | R013 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | hdong线41/42间开关 | hdong线41杆 | PZXL-00154-N0040 | hdong线42杆 | PZXL-00154-N0192 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸支持；含raw名称纠正 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00154-SW-R014 | R014 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | hdong线73/74间开关 | hdong线73杆 | PZXL-00154-N0074 | hdong线74杆 | PZXL-00154-N0080 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸支持主干开关连接 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00161-SW-R016 | R016 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | hpao线36开关 | hpao线36杆 | PZXL-00161-N0036 | hpao线37杆 | PZXL-00161-N0037 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00161-SW-R017 | R017 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | hpao线42开关 | hpao线42杆 | PZXL-00161-N0042 | hpao线43杆 | PZXL-00161-N0043 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00161-SW-R018 | R018 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | hpao线43开关（三遥） | hpao线43杆 | PZXL-00161-N0043 | hpao线44杆 | PZXL-00161-N0044 | 分段开关 | YES | NEED_CONFIRM | CLOSED | YES | 0 | 0 | 0 | 图纸确认三遥开关 | HIGH | YES | YES | EXACT_CANONICAL/EXACT_CANONICAL
PZXL-00173-SW-R021 | R021 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | hzhen线73开关 | 10kVhzhen线73#杆 | PZXL-00173-N0071 | 10kVhzhen线74#杆 | PZXL-00173-N0072 | 分段开关 | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认 | HIGH | YES | YES | EXACT_CANONICAL/NORMALIZED_UNIQUE
PZXL-00161-SW-R020A | R020 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | R020_43杆至2分支箱设备连接 | hpao线43杆 | PZXL-00161-N0043 | VIRTUAL::hpao线2分支箱 | PZXL-00161-V001 | BRANCH_BOX_LINK | YES | NEED_CONFIRM | CLOSED | NO | 0 | 0 | 0 | 图纸：hpao 43附近分支箱链；具体内部设备连接按拓扑等值，不赋予线路长度 | MEDIUM_HIGH | YES | YES | EXACT_CANONICAL
PZXL-00161-SW-R020B | R020 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | R020_2分支箱至王场湖支线1分支开关 | VIRTUAL::hpao线2分支箱 | PZXL-00161-V001 | VIRTUAL::hpao线王场湖支线1分支开关 | PZXL-00161-V002 | DEVICE_LINK | YES | NEED_CONFIRM | CLOSED | UNKNOWN | 0 | 0 | 0 | 图纸确认王场湖支线分支开关位于分支箱侧；内部长度未知按零长度设备连接 | MEDIUM_HIGH | YES | YES | VIRTUAL
PZXL-00161-SW-R020C | R020 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | hpao线王场湖支线1分支开关（三遥） | VIRTUAL::hpao线王场湖支线1分支开关 | PZXL-00161-V002 | hpao线王场湖支线1杆 | PZXL-00161-N0072 | BRANCH_SWITCH | YES | NEED_CONFIRM | CLOSED | YES | 0 | 0 | 0 | 图纸明确标注“hpao线王场湖支线1分支开关（三遥）” | HIGH | YES | YES | EXACT_CANONICAL

## 17_tie_master
tie_id | scope | from_station | from_station_id | from_feeder_id | from_feeder_alias | from_node_query | from_node_id | from_raw_locator | to_station | to_station_id | to_feeder_id | to_feeder_alias | to_node_query | to_node_id | to_raw_locator | connection_type | normal_state | state_status | confidence | evidence | current_v2_crossref | model_priority | endpoint_resolution | allow_in_base | requires_revalidation
TIE-001 | 站间 | 墩集变 | BDZ-00027 | PZXL-00099 | dzhen | dzhen线王场湖支线17杆 | NEED_CONFIRM | 24-13-17 | 河湾变 | BDZ-00048 | PZXL-00154 | hdong | hdong线93杆 | PZXL-00154-N0105 | 93 | 联络开关 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | HIGH | 上一轮结构化现场记录双侧闭环；当前图纸/V2对应王场湖支线17↔河东93 | V2:T02 | P1 | AMBIGUOUS_OR_NOT_FOUND/EXACT_CANONICAL | NO | YES
TIE-002 | 站间 | 墩集变 | BDZ-00027 | PZXL-00092 | dnan | dnan线合金厂支线4杆 | PZXL-00092-N0146 | 42-4 | 河湾变 | BDZ-00048 | PZXL-00161 | hpao | hpao线59杆 | PZXL-00161-N0059 | 59 | 联络开关 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | HIGH | 上一轮结构化现场记录双侧闭环；当前V2两侧路径均可达 | V2:T01 | P0_FIRST_CASE | EXACT_CANONICAL/EXACT_CANONICAL | NO | NO
TIE-003 | 站间 | 墩集变 | BDZ-00027 | PZXL-00097 | dxi | dxi线王场湖支线14 | PZXL-00097-N0187 | 15-37-14/WCH14 | 河湾变 | BDZ-00048 | PZXL-00161 | hpao | hpao线王场湖支线1杆 | PZXL-00161-N0072 | WCH1 | 联络开关 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | MEDIUM_HIGH | 双侧记录；当前V2确认联络，hpao侧需R020设备链修复 | V2:T03 | P1 | EXACT_CANONICAL/EXACT_CANONICAL | NO | NO
TIE-004 | 站间 | 墩集变 | BDZ-00027 | PZXL-00099 | dzhen | NEED_CONFIRM | NEED_CONFIRM | 24-15-10-4 | 河湾变 | BDZ-00048 | PZXL-00173 | hzhen | NEED_CONFIRM | NEED_CONFIRM | 待定位 | 隔离/母线连接 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | MEDIUM | 上一轮单侧现场记录；当前V2未形成闭环，保留为待复核候选 | NOT_IN_CURRENT_V2 | P2_REVALIDATE | LOCATOR_ONLY/LOCATOR_ONLY | NO | YES
TIE-005 | 站内 | 墩集变 | BDZ-00027 | PZXL-00099 | dzhen | NEED_CONFIRM | NEED_CONFIRM | 15-14 | 墩集变 | BDZ-00027 | PZXL-00097 | dxi | NEED_CONFIRM | NEED_CONFIRM | 15-15-2附近 | 隔离/开闭所 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | MEDIUM | 上一轮双侧近似记录；当前V2对应智能制造产业园开闭所母联/双电源迹象 | V2:T05 | P2 | LOCATOR_ONLY/LOCATOR_ONLY | NO | YES
TIE-006 | 站内 | 墩集变 | BDZ-00027 | PZXL-00092 | dnan | NEED_CONFIRM | NEED_CONFIRM | 26-5附近 | 墩集变 | BDZ-00027 | PZXL-00097 | dxi | NEED_CONFIRM | NEED_CONFIRM | 15-31-4附近 | 配电室母线连接 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | MEDIUM | 上一轮双侧近似记录；当前新图纸需重新落位 | NOT_IN_CURRENT_V2 | P2_REVALIDATE | LOCATOR_ONLY/LOCATOR_ONLY | NO | YES
TIE-007 | 站内 | 河湾变 | BDZ-00048 | PZXL-00154 | hdong | hdong线48杆 | PZXL-00154-N0193 | 48 | 河湾变 | BDZ-00048 | PZXL-00173 | hzhen | 10kVhzhen线49#杆 | PZXL-00173-N0047 | 49 | 联络开关 | CLOSED | CONFIRMED_PREVIOUS_FIELD_INPUT | HIGH | 上一轮正常状态已确认合闸；当前V2双侧图纸完全对应 | V2:T04 | P0_BASE_TOPOLOGY | EXACT_CANONICAL/EXACT_CANONICAL | YES | NO
TIE-008 | 站内 | 河湾变 | BDZ-00048 | PZXL-00154 | hdong | NEED_CONFIRM | NEED_CONFIRM | 56-1附近 | 河湾变 | BDZ-00048 | PZXL-00173 | hzhen | NEED_CONFIRM | NEED_CONFIRM | 56 | 开闭所/隔离 | OPEN | CONFIRMED_PREVIOUS_FIELD_INPUT | HIGH | 上一轮双侧记录且正常分闸；当前V2未单列，保留防止与TIE-007重复计入 | NOT_IN_CURRENT_V2 | P2_REVALIDATE | LOCATOR_ONLY/LOCATOR_ONLY | NO | YES

## 18_source_master
source_id | station_id | station_name | feeder_id | feeder_alias | feeder_name | root_node_name | root_node_id | base_kv | station_capacity_mva | station_2025_max_load_mw | station_2025_min_load_mw | feeder_2025_max_p_raw_mw | feeder_2025_max_current_a | feeder_max_allowed_current_a | feeder_model_boundary_p_mw | feeder_boundary_source_status | q_rule | station_n1_source | root_status | resolution_method
SRC-PZXL-00092 | BDZ-00027 | 墩集变 | PZXL-00092 | dnan | 墩南线 | dnan线01杆 | PZXL-00092-N0016 | 10 | 100 | 59.21 | -37.27 | 6.5296 | 392.52 | 485 | 6.5296 | SRC06_2025_MAX_P | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL
SRC-PZXL-00099 | BDZ-00027 | 墩集变 | PZXL-00099 | dzhen | 墩振线 | dzhen线01杆 | PZXL-00099-N0001 | 10 | 100 | 59.21 | -37.27 | 8.2344 | 507 | 595 | 8.2344 | SRC06_2025_MAX_P | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL
SRC-PZXL-00097 | BDZ-00027 | 墩集变 | PZXL-00097 | dxi | 墩西线 | dxi线01杆 | PZXL-00097-N0044 | 10 | 100 | 59.21 | -37.27 | 3.3938 | 208.56 | 485 | 3.3938 | SRC06_2025_MAX_P | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL
SRC-PZXL-00154 | BDZ-00048 | 河湾变 | PZXL-00154 | hdong | 河东线 | hdong线1杆 | PZXL-00154-N0016 | 10 | 150 | 73.74 | -5.22 | 0 | 544.57 | 600 | 8.9606 | DERIVED_FROM_2025_MAX_CURRENT_AT_PF0.95; RAW_P=0_ANOMALY | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL
SRC-PZXL-00161 | BDZ-00048 | 河湾变 | PZXL-00161 | hpao | 河炮线 | hpao线01杆 | PZXL-00161-N0001 | 10 | 150 | 73.74 | -5.22 | 1.8876 | 126.21 | 595 | 1.8876 | SRC06_2025_MAX_P | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL
SRC-PZXL-00173 | BDZ-00048 | 河湾变 | PZXL-00173 | hzhen | 河镇线 | 10kVhzhen线01#杆 | PZXL-00173-N0001 | 10 | 150 | 73.74 | -5.22 | 6.2899 | 365.98 | 605 | 6.2899 | SRC06_2025_MAX_P | 实际Q优先；缺Q时PF=0.95，敏感性0.90/0.95/0.98。 | 设备台账N-1=是；实际N-1可转供由主变+网络联络联合校核，不用CLR=2.0反推。 | CONFIRMED | EXACT_CANONICAL

## 19_injection_summary
feeder_id | feeder_alias | model_boundary_p_mw | boundary_p_source | pv_total_or_anchor | pv_status | load_seed_file | pv_seed_file | q_rule | quality_note
PZXL-00092 | dnan | 6.5296 | SRC06_2025_MAX_P | 7.34 MW actual PV output peak anchor; installed capacity incomplete | OUTPUT_ANCHOR_ONLY | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot
PZXL-00099 | dzhen | 8.2344 | SRC06_2025_MAX_P | 6650 kVA total; 6600 kVA node-located + 50 residual | NEAR_COMPLETE | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot
PZXL-00097 | dxi | 3.3938 | SRC06_2025_MAX_P | >=3700 kVA located lower bound | LOWER_BOUND | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot
PZXL-00154 | hdong | 8.9606 | DERIVED_FROM_2025_MAX_CURRENT_AT_PF0.95; RAW_P=0_ANOMALY | 1890 kVA feeder total, aggregated near 42-7-1 | AGGREGATED | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot
PZXL-00161 | hpao | 1.8876 | SRC06_2025_MAX_P | 0 kVA | CONFIRMED_ZERO | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot
PZXL-00173 | hzhen | 6.2899 | SRC06_2025_MAX_P | 2500 kVA feeder total, aggregated at known PV-related branch | AGGREGATED | node_load_seed_pf095.csv | node_pv_seed.csv | PF0.95 base; 0.90/0.98 sensitivity | annual max feeder P is a stress boundary, not a synchronous six-feeder snapshot

## 20_conductor_master
conductor_key | raw_model | normalized_model | electrical_proxy | span_count | total_length_km | feeders | r_pf_ohm_per_km | x_pf_ohm_per_km | imax_base_a | imax_upper_ref_a | thermal_base_mva_at_10kv | thermal_upper_mva_at_10kv | r20_reference | parameter_grade | mapping_rule | sensitivity_rule | formal_use_rule | source_r_x | source_imax | source_mapping
COND-01 | JKLGYJ-240 | JKLGYJ-10-240/30 | JKLYJ-240/10 (240 mm² insulated overhead typical library) | 155 | 7.75 | hdong | 0.13 | 0.356 | 500 | 550 | 8.6603 | 9.5263 | ~0.125 class / conductor-family reference | B | raw省略10kV与钢芯截面；按10kV工程常见240/30映射 | R ±10%; X ±15%; Imax 500~550 A | 规划案例可用；若成为最终瓶颈，优先按台账/厂家复核 | https://patents.google.com/patent/CN116581754A/zh | https://upload.xuancheng.gov.cn/download?id=693357&siteId=6 | https://ggzy.ht.gov.cn/jyxx/001004/001004001/20260610/45de60d1-eae9-46a8-8704-cc5323d3b243.html
COND-02 | JKLGYJ-70 | JKLGYJ-10-70/10 | 70 mm² insulated steel-core overhead | 12 | 0.6 | dzhen | 0.443 | 0.397 | 245 | 247.5 | 4.2435 | 4.2868 | 0.443 Ω/km class | B | raw省略10kV与钢芯截面；按10kV工程常见70/10映射 | R ±10%; X 0.34~0.44 Ω/km; Imax 220~247.5 A | 规划案例可用；非关键主干 | R按70 mm²铝导体标准族；X为10kV架空线典型值（几何缺失） | https://upload.xuancheng.gov.cn/download?id=693357&siteId=6 | https://www.jl.gov.cn/ggzy/sysggzy/sysjyxx/sysgcjs/ccsgczbgg/202605/t20260528_9636242.html
COND-03 | JKLYJ-150 | JKLYJ-10-150 | exact typical-library match | 6 | 0.3 | hpao | 0.26368 | 0.29584 | 285 | 400 | 4.9363 | 6.9282 | 0.206 Ω/km standard conductor reference; PF library uses 0.26368 | A/B | 直接等价命名 | R/X用典型参数库；Imax 285~400 A | R/X可直接用于规划潮流；Imax必须做285/400两档敏感性 | https://patents.google.com/patent/CN116581754A/zh | https://upload.xuancheng.gov.cn/download?id=693357&siteId=6 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=498F0E9BDCC9F878D7A6272E0AEC46AD
COND-04 | JKLYJ-240/10 | JKLYJ-10-240 (raw写法与典型库JKLYJ-240/10等价) | exact typical-library match | 3 | 0.15 | dzhen | 0.13 | 0.356 | 500 | 550 | 8.6603 | 9.5263 | 0.125 Ω/km class | A/B | 240/10解释为240 mm²、10kV的历史/系统写法，不解释为钢芯240/10 | R ±5%; X ±15%; Imax 500~550 A | 规划案例可直接使用 | https://patents.google.com/patent/CN116581754A/zh | https://upload.xuancheng.gov.cn/download?id=648384&siteId=3 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=498F0E9BDCC9F878D7A6272E0AEC46AD
COND-05 | JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | JKLYJ-240/10 electrical conductor equivalent | 841 | 43.94 | dnan,dxi,dzhen,hzhen | 0.13 | 0.356 | 500 | 550 | 8.6603 | 9.5263 | 0.125 Ω/km class | B+ | Q为绝缘结构/耐候类别差异，导电芯按240 mm² JKLYJ等效 | 关键主干：Imax必须同时跑500 A与550 A；X ±15% | 本案例关键主干，可作为规划基准；报告明确为典型参数而非实测 | https://patents.google.com/patent/CN116581754A/zh | https://upload.xuancheng.gov.cn/download?id=648384&siteId=3 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=498F0E9BDCC9F878D7A6272E0AEC46AD
COND-06 | JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | JKLYJ-240/10 electrical conductor equivalent | 5 | 0.25 | hpao | 0.13 | 0.356 | 500 | 550 | 8.6603 | 9.5263 | 0.125 Ω/km class | B | QN绝缘/结构变体按240 mm²导电芯等效 | Imax 500~550 A；X ±15% | 规划案例可用；仅0.25 km | https://patents.google.com/patent/CN116581754A/zh | https://upload.xuancheng.gov.cn/download?id=648384&siteId=3 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=498F0E9BDCC9F878D7A6272E0AEC46AD
COND-07 | JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | 高导电率钢芯铝绞线240/40 | 39 | 1.95 | hdong | 0.1232 | 0.356 | 550 | 595.22 | 9.5263 | 10.3095 | 0.1171 Ω/km; literature AC resistance 0.1232 Ω/km | B | GIA按G1A；保留GD，原始名称更像高导电率JL(GD)/G1A而非普通JL/G1A | R用0.1232；X ±15%；Imax 550~595.22 A | Imax采用普通240/40的保守参考，高导电率同几何不应更低；瓶颈时复核 | https://pdf.hanspub.org/tdet20200200000_87962235.pdf | https://hbj.yzcity.gov.cn/hbj/031005/202506/f53fbe5f8fab47c696d9720a7c11fad6/files/dd041c21d3304b01a96e41ee0fa8e614.pdf | https://pdf.hanspub.org/tdet20200200000_87962235.pdf
COND-08 | JL/G1A-240/30 | JL/G1A-240/30 | exact bare ACSR family | 6 | 0.3 | hpao | 0.13 | 0.356 | 550 | 562 | 9.5263 | 9.7341 | 0.1181 Ω/km | B+ | 直接规范化 | PF模型R取0.13保守高于20℃直流0.1181；X ±15%；Imax 550~562 A | 规划案例可用 | https://sthjj.huhhot.gov.cn/ywgz/hjyxpj/xmslqk/202511/P020251127380578958416.pdf | https://sthjj.quanzhou.gov.cn/hjgl/hbsp/hpslqkgk/202606/P020260618423129515361.pdf | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=F936B58052E9B750D1FEF196B660A084
COND-09 | JLB3-35 | JLB3-35 (疑似地线/铝包钢类，不应作为10kV相导线瓶颈) | JL(GD)/G1A-240/40 adjacent phase-span proxy | 1 | 0.05 | hdong | 0.1232 | 0.356 | 550 | 595.22 | 9.5263 | 10.3095 | raw JLB3 not used as phase conductor | C-PROXY | 该型号仅hdong源端1→2一档50m，后一档立即为JL(GD)/G1A-240/40；按相导线连续性代理 | 如该50m边成为瓶颈，立即停止正式结论并人工复核 | 禁止使用JLB3-35自身地线参数限制相功率；使用相邻主干代理 | https://pdf.hanspub.org/tdet20200200000_87962235.pdf | https://hbj.yzcity.gov.cn/hbj/031005/202506/f53fbe5f8fab47c696d9720a7c11fad6/files/dd041c21d3304b01a96e41ee0fa8e614.pdf | current structured topology adjacency
COND-10 | JLRX/T-120/30 | JLRX/T-120/30 (碳纤维复合芯耐热导线家族) | conservative 120 mm² insulated-overhead proxy | 1 | 0.05 | dzhen | 0.33 | 0.38 | 300 | 350 | 5.1962 | 6.0622 | not located for exact 120/30 variant | C-PROXY | JLRX/T家族可确认，但120/30精确型式参数未检得；仅1档50m分支，采用保守120 mm²代理 | R 0.30~0.38; X 0.32~0.44; Imax 300~350 A | 若该支路进入关键转供路径或成为瓶颈，需单独复核 | engineering conservative proxy; exact family supported by patent | https://upload.xuancheng.gov.cn/download?id=693357&siteId=6 | https://patents.google.com/patent/CN105529651A/zh
COND-11 | LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | JL/G1A-240/30 | 55 | 2.75 | hpao | 0.13 | 0.356 | 550 | 562 | 9.5263 | 9.7341 | 0.1181 Ω/km | B+ | 10表示10kV工程语境，240为铝截面；按10kV工程常见LGJ-240/30映射 | 关键hpao主干：Imax 550/562两档；X ±15% | 本案例关键主干，可作为规划基准 | https://sthjj.huhhot.gov.cn/ywgz/hjyxpj/xmslqk/202511/P020251127380578958416.pdf | https://sthjj.quanzhou.gov.cn/hjgl/hbsp/hpslqkgk/202606/P020260618423129515361.pdf | https://www.ggzy.gov.cn/information/deal/html/b/0067/0101/20260604/00679edf62f7e5a847868b19d27564377738.html

## 21_assumptions_debug
assumption_id | item | base_value_or_rule | sensitivity | status | formal_label | note
A01 | 缺Q时负荷功率因数 | 0.95 | 0.90/0.98 | ACTIVE | PLANNING_ASSUMPTION | 实际Q可覆盖
A02 | 节点负荷空间分布 | 现场观察配变kVA权重 | uniform-leaf | ACTIVE | PLANNING_ASSUMPTION | 总P与馈线边界严格闭合
A03 | hdong馈线最大P | sqrt(3)*10kV*544.57A*0.95 | PF0.90/0.98 | ANOMALY_PROXY | PLANNING_PROXY | 原始最大P=0不可用
A04 | PV无功 | unity PF | 必要时再加Q控制 | ACTIVE | PLANNING_ASSUMPTION
A05 | 年度馈线极值同步性 | 禁止视为同步 | N/A | FIXED_RULE | DATA_QUALITY_RULE | 采用规划包络场景
A06 | 线路有效热限 | min(导线Imax,馈线最大允许电流) | 导线upper | ACTIVE | PLANNING_CONSERVATIVE | 具体开关成为瓶颈时定点复核

## 22_scenario_master
scenario_id | scenario_name | purpose | load_boundary_rule | pv_rule | station_boundary_rule | line_limit_rule | voltage_rule | q_rule | synchronization_status | formal_use
S0_TOPOLOGY_ONLY | 基准拓扑审计 | 正常开关状态、孤岛、环路、源端可达性 | 不要求负荷数值 | 不要求PV | 不启用 | 不启用 | 不启用 | 不启用 | N/A | YES_TOPOLOGY
S1_FEEDER_STRESS | 馈线正向应力包络 | 局部联络正向转供及热稳/电压能力 | 六线采用SRC06历史最大P；hdong用544.57A×10kV×√3×PF0.95代理；节点按现场kVA权重 | PV factor=0基准，另做0.1敏感性 | 站级容量/年度峰值作容量筛查，不宣称同一历史时刻 | min(导线Imax_base,SRC06馈线最大允许电流) | 硬0.93~1.07pu；优选0.95~1.05pu | PF0.95；0.90/0.98敏感性 | ENVELOPE_NOT_HISTORICAL_SYNCHRONOUS | PLANNING_ENVELOPE
S2_REVERSE_PV | 高PV反送应力 | 反向潮流、过电压、反向转供 | S1空间权重，load_factor=0.3/0.5/0.7 | 已知PV容量×0.8/0.9/1.0；dnan可用7.34MW峰值锚点；hpao=0 | 2025站级最小净负荷与2026PV典型记录仅作边界一致性校核 | 同S1 | 0.93~1.07pu | 负荷PF0.95；PV unity PF基准 | PLANNING_SCENARIO_WITH_REAL_ANCHORS | PLANNING_STRESS
S3_TRANSFER_SWEEP | 联络最大转供扫描 | 识别最大转供与首个绑定约束 | 分别以S1/S2基础状态扫描 | 继承基础场景 | 同时检查站端容量和N-1筛查边界 | effective_rate_a_base；另跑upper sensitivity | 0.93~1.07pu | 继承 | SCENARIO_BASED | YES_PLANNING

## 23_qa_gate
qa_id | priority | category | issue | status | impact | prepared_resolution | remaining_action
QF01 | P0 | STATION_MAPPING | 河湾变脱敏站码 | PASS | 原V5占位ID | 河东/河炮/河镇SRC06起点站码均为BDZ-00048，V5.1已锁定 | NONE
QF02 | P0 | FEEDER_BOUNDARY | 六线P/I/运行限额 | PASS_WITH_ANOMALY_GUARD | 潮流/热限基础 | 六线已提取；hdong P=0与电流/负载率冲突，规划P用I×PF0.95代理 | 有实际hdong P时覆盖代理
QF03 | P0 | LINE_LIMIT | 设备/馈线运行限额 | PASS_PLANNING | 防止仅按导线Imax高估 | 1124边effective_rate=min(导线Imax,SRC06馈线最大允许电流) | 具体开关若成为瓶颈再定点核铭牌
QF04 | P0 | STATION_BOUNDARY | 两站/四主变边界 | PASS | 站端与N-1筛查 | 站/主变容量、年度极值、单母分段、N-1台账均入库 | 精确馈线→母线段→主变映射未找到
QF05 | P0 | LOAD_SPATIAL | 节点负荷空间分布 | PASS_PLANNING_SEED | 压降/支路潮流 | 旧现场容量观察映射到当前节点；缺细分子节点时聚合至父主杆；按kVA权重闭合至馈线P | 若分布成为约束，跑uniform-leaf敏感性
QF06 | P0 | PV_SPATIAL | PV位置/容量 | PARTIAL_BUT_SCENARIO_READY | 反向潮流/电压 | dzhen已定位6600/6650kVA；hdong/hzhen总量聚合；hpao=0；dnan有7.34MW峰值锚点 | dnan完整装机总量无法严格恢复
QF07 | P0 | SWITCH_STATE | 8处关键联络状态 | PASS | 基准拓扑 | 7 OPEN + TIE-007 CLOSED已继承 | 普通切分开关按图纸符号校准
QF08 | P0 | TOPOLOGY | TIE-002 | PASS_FIRST_CASE | 首个规划案例 | 两侧路径、线路参数、馈线边界、节点注入种子、站端边界均已准备 | NONE before calculation
QF09 | P1 | TOPOLOGY | TIE-001/TIE-003局部断点 | PARTIAL | 后续两通道 | R005/R010-R014/R020已进入patch任务 | 按图纸闭环后计算
QF10 | P1 | SYNCHRONIZATION | 无六线同时间戳P/Q断面 | NO_LONGER_BLOCKS_PLANNING | 不能声称历史真实同步断面 | 改用明确包络/规划场景，禁止把年度极值相加冒充同步 | 后续若有SCADA同步断面可直接替换
QF11 | P1 | BUS_SECTION | 馈线→10kV母线段→具体主变归属 | REAL_REMAINING_GAP | 单台主变N-1精确归因 | 局部案例先用站级聚合边界；站内单母分段和主变组合已知 | 需要精确到单台主变时从一次接线/DMS补映射

## 24_agent_tasks
task_id | priority | task | instruction | inputs | outputs | gate
A0 | P0 | 完整性检查 | 核验manifest、六馈线/两站主键、1124边100%参数化 | prepared data masters | import_report.json | fail-stop
A1 | P0 | 基准拓扑构建 | 加载physical_edges+switches+ties；TIE-007必须CLOSED，其余按确认状态 | physical/switch/tie masters | base_operational_graph | 环路/孤岛审计
A2 | P0 | 普通开关图例校准 | 用TIE-007(CLOSED)和TIE-001/002/003(OPEN)反标图纸黑/空白语义 | drawings + switch_state_fusion | switch_symbol_patch.csv | 锚点一致才批量应用
A3 | P0 | 负荷/PV注入生成 | 直接读取node_load_seed_pf095 + node_pv_seed；不再重新抽旧脱敏数据 | prepared injection seeds | injection_cases.csv | 馈线总P闭合
A4 | P0 | TIE-002基准/转供扫描 | S1/S2分别闭合TIE-002并枚举切分点保持辐射，求双向最大转供 | S1/S2 + TIE-002 | case_TIE002_results.csv | 输出绑定约束
A5 | P0 | 敏感性 | PF 0.90/0.95/0.98、X±15%、Imax base/upper、uniform-leaf空间对照 | scenario parameters | TIE002_sensitivity.csv | 结论稳定性
A6 | P1 | TIE-001拓扑闭环 | 完成R005/R010-R014设备边修复后计算 | drawings | topology_patch_log.csv | 路径连通
A7 | P1 | TIE-003拓扑闭环 | 正式核R020设备链后计算 | drawings | topology_patch_log.csv | 路径连通
A8 | P2 | 三通道联合互济 | 共同站级容量、线路、电压、径向约束下联合求解；禁止简单相加 | three tie cases | station_mutual_aid_results.csv | 单通道通过
A9 | P0 | 结果追溯 | 记录场景、参数等级、源数据、patch、solver版本、假设 | all | run_manifest.json | 可复现

## 25_base_debug_edges
model_edge_id | edge_type | from_node_id | to_node_id | asset_ref | normal_state | debug_state | active_in_debug_base | length_m | conductor_model | parameter_status | evidence
PZXL-00092-B0001 | PHYSICAL_SPAN | PZXL-00092-N0030 | PZXL-00092-N0025 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0002 | PHYSICAL_SPAN | PZXL-00092-N0038 | PZXL-00092-N0039 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0003 | PHYSICAL_SPAN | PZXL-00092-N0061 | PZXL-00092-N0062 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0004 | PHYSICAL_SPAN | PZXL-00092-N0263 | PZXL-00092-N0262 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0005 | PHYSICAL_SPAN | PZXL-00092-N0091 | PZXL-00092-N0092 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0006 | PHYSICAL_SPAN | PZXL-00092-N0263 | PZXL-00092-N0264 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0007 | PHYSICAL_SPAN | PZXL-00092-N0060 | PZXL-00092-N0061 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0008 | PHYSICAL_SPAN | PZXL-00092-N0030 | PZXL-00092-N0031 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0009 | PHYSICAL_SPAN | PZXL-00092-N0034 | PZXL-00092-N0035 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0010 | PHYSICAL_SPAN | PZXL-00092-N0224 | PZXL-00092-N0225 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0011 | PHYSICAL_SPAN | PZXL-00092-N0251 | PZXL-00092-N0252 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0012 | PHYSICAL_SPAN | PZXL-00092-N0135 | PZXL-00092-N0136 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0013 | PHYSICAL_SPAN | PZXL-00092-N0232 | PZXL-00092-N0242 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0014 | PHYSICAL_SPAN | PZXL-00092-N0138 | PZXL-00092-N0139 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0015 | PHYSICAL_SPAN | PZXL-00092-N0143 | PZXL-00092-N0144 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0016 | PHYSICAL_SPAN | PZXL-00092-N0068 | PZXL-00092-N0069 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0017 | PHYSICAL_SPAN | PZXL-00092-N0069 | PZXL-00092-N0070 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0018 | PHYSICAL_SPAN | PZXL-00092-N0062 | PZXL-00092-N0143 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0019 | PHYSICAL_SPAN | PZXL-00092-N0083 | PZXL-00092-N0084 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0020 | PHYSICAL_SPAN | PZXL-00092-N0063 | PZXL-00092-N0064 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0021 | PHYSICAL_SPAN | PZXL-00092-N0073 | PZXL-00092-N0074 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0022 | PHYSICAL_SPAN | PZXL-00092-N0082 | PZXL-00092-N0083 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0023 | PHYSICAL_SPAN | PZXL-00092-N0072 | PZXL-00092-N0073 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0024 | PHYSICAL_SPAN | PZXL-00092-N0064 | PZXL-00092-N0065 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0025 | PHYSICAL_SPAN | PZXL-00092-N0070 | PZXL-00092-N0071 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0026 | PHYSICAL_SPAN | PZXL-00092-N0071 | PZXL-00092-N0072 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0027 | PHYSICAL_SPAN | PZXL-00092-N0065 | PZXL-00092-N0068 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0028 | PHYSICAL_SPAN | PZXL-00092-N0084 | PZXL-00092-N0087 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0029 | PHYSICAL_SPAN | PZXL-00092-N0062 | PZXL-00092-N0063 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0030 | PHYSICAL_SPAN | PZXL-00092-N0074 | PZXL-00092-N0082 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0031 | PHYSICAL_SPAN | PZXL-00092-N0023 | PZXL-00092-N0024 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0032 | PHYSICAL_SPAN | PZXL-00092-N0184 | PZXL-00092-N0185 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0033 | PHYSICAL_SPAN | PZXL-00092-N0038 | PZXL-00092-N0160 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0034 | PHYSICAL_SPAN | PZXL-00092-N0216 | PZXL-00092-N0217 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0035 | PHYSICAL_SPAN | PZXL-00092-N0016 | PZXL-00092-N0017 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0036 | PHYSICAL_SPAN | PZXL-00092-N0055 | PZXL-00092-N0056 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0037 | PHYSICAL_SPAN | PZXL-00092-N0048 | PZXL-00092-N0049 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0038 | PHYSICAL_SPAN | PZXL-00092-N0141 | PZXL-00092-N0142 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0039 | PHYSICAL_SPAN | PZXL-00092-N0093 | PZXL-00092-N0094 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0040 | PHYSICAL_SPAN | PZXL-00092-N0043 | PZXL-00092-N0044 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0041 | PHYSICAL_SPAN | PZXL-00092-N0035 | PZXL-00092-N0036 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0042 | PHYSICAL_SPAN | PZXL-00092-N0139 | PZXL-00092-N0140 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0043 | PHYSICAL_SPAN | PZXL-00092-N0219 | PZXL-00092-N0220 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0044 | PHYSICAL_SPAN | PZXL-00092-N0222 | PZXL-00092-N0223 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0045 | PHYSICAL_SPAN | PZXL-00092-N0234 | PZXL-00092-N0235 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0046 | PHYSICAL_SPAN | PZXL-00092-N0148 | PZXL-00092-N0149 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0047 | PHYSICAL_SPAN | PZXL-00092-N0033 | PZXL-00092-N0034 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0048 | PHYSICAL_SPAN | PZXL-00092-N0024 | PZXL-00092-N0030 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0049 | PHYSICAL_SPAN | PZXL-00092-N0136 | PZXL-00092-N0137 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0050 | PHYSICAL_SPAN | PZXL-00092-N0153 | PZXL-00092-N0154 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0051 | PHYSICAL_SPAN | PZXL-00092-N0001 | PZXL-00092-N0002 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0052 | PHYSICAL_SPAN | PZXL-00092-N0140 | PZXL-00092-N0141 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0053 | PHYSICAL_SPAN | PZXL-00092-N0015 | PZXL-00092-N0001 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0054 | PHYSICAL_SPAN | PZXL-00092-N0133 | PZXL-00092-N0147 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0055 | PHYSICAL_SPAN | PZXL-00092-N0005 | PZXL-00092-N0006 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0056 | PHYSICAL_SPAN | PZXL-00092-N0032 | PZXL-00092-N0033 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0057 | PHYSICAL_SPAN | PZXL-00092-N0037 | PZXL-00092-N0038 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0058 | PHYSICAL_SPAN | PZXL-00092-N0228 | PZXL-00092-N0229 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0059 | PHYSICAL_SPAN | PZXL-00092-N0039 | PZXL-00092-N0040 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0060 | PHYSICAL_SPAN | PZXL-00092-N0040 | PZXL-00092-N0041 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0061 | PHYSICAL_SPAN | PZXL-00092-N0220 | PZXL-00092-N0221 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0062 | PHYSICAL_SPAN | PZXL-00092-N0229 | PZXL-00092-N0230 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0063 | PHYSICAL_SPAN | PZXL-00092-N0003 | PZXL-00092-N0004 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0064 | PHYSICAL_SPAN | PZXL-00092-N0042 | PZXL-00092-N0043 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0065 | PHYSICAL_SPAN | PZXL-00092-N0137 | PZXL-00092-N0138 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0066 | PHYSICAL_SPAN | PZXL-00092-N0151 | PZXL-00092-N0152 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0067 | PHYSICAL_SPAN | PZXL-00092-N0152 | PZXL-00092-N0153 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0068 | PHYSICAL_SPAN | PZXL-00092-N0154 | PZXL-00092-N0155 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0069 | PHYSICAL_SPAN | PZXL-00092-N0227 | PZXL-00092-N0228 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0070 | PHYSICAL_SPAN | PZXL-00092-N0036 | PZXL-00092-N0037 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0071 | PHYSICAL_SPAN | PZXL-00092-N0226 | PZXL-00092-N0227 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0072 | PHYSICAL_SPAN | PZXL-00092-N0235 | PZXL-00092-N0236 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0073 | PHYSICAL_SPAN | PZXL-00092-N0037 | PZXL-00092-N0243 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0074 | PHYSICAL_SPAN | PZXL-00092-N0031 | PZXL-00092-N0032 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0075 | PHYSICAL_SPAN | PZXL-00092-N0231 | PZXL-00092-N0232 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0076 | PHYSICAL_SPAN | PZXL-00092-N0134 | PZXL-00092-N0135 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0077 | PHYSICAL_SPAN | PZXL-00092-N0230 | PZXL-00092-N0231 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0078 | PHYSICAL_SPAN | PZXL-00092-N0218 | PZXL-00092-N0219 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0079 | PHYSICAL_SPAN | PZXL-00092-N0002 | PZXL-00092-N0003 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0080 | PHYSICAL_SPAN | PZXL-00092-N0221 | PZXL-00092-N0222 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0081 | PHYSICAL_SPAN | PZXL-00092-N0048 | PZXL-00092-N0224 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0082 | PHYSICAL_SPAN | PZXL-00092-N0242 | PZXL-00092-N0233 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0083 | PHYSICAL_SPAN | PZXL-00092-N0133 | PZXL-00092-N0134 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0084 | PHYSICAL_SPAN | PZXL-00092-N0150 | PZXL-00092-N0151 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0085 | PHYSICAL_SPAN | PZXL-00092-N0041 | PZXL-00092-N0042 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0086 | PHYSICAL_SPAN | PZXL-00092-N0147 | PZXL-00092-N0148 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0087 | PHYSICAL_SPAN | PZXL-00092-N0149 | PZXL-00092-N0150 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0088 | PHYSICAL_SPAN | PZXL-00092-N0004 | PZXL-00092-N0005 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0089 | PHYSICAL_SPAN | PZXL-00092-N0225 | PZXL-00092-N0226 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0090 | PHYSICAL_SPAN | PZXL-00092-N0210 | PZXL-00092-N0211 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0091 | PHYSICAL_SPAN | PZXL-00092-N0177 | PZXL-00092-N0178 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0092 | PHYSICAL_SPAN | PZXL-00092-N0182 | PZXL-00092-N0183 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0093 | PHYSICAL_SPAN | PZXL-00092-N0049 | PZXL-00092-N0050 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0094 | PHYSICAL_SPAN | PZXL-00092-N0183 | PZXL-00092-N0184 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0095 | PHYSICAL_SPAN | PZXL-00092-N0209 | PZXL-00092-N0210 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0096 | PHYSICAL_SPAN | PZXL-00092-N0087 | PZXL-00092-N0088 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0097 | PHYSICAL_SPAN | PZXL-00092-N0022 | PZXL-00092-N0023 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0098 | PHYSICAL_SPAN | PZXL-00092-N0094 | PZXL-00092-N0095 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0099 | PHYSICAL_SPAN | PZXL-00092-N0213 | PZXL-00092-N0214 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0100 | PHYSICAL_SPAN | PZXL-00092-N0176 | PZXL-00092-N0177 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0101 | PHYSICAL_SPAN | PZXL-00092-N0101 | PZXL-00092-N0102 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0102 | PHYSICAL_SPAN | PZXL-00092-N0090 | PZXL-00092-N0091 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0103 | PHYSICAL_SPAN | PZXL-00092-N0179 | PZXL-00092-N0180 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0104 | PHYSICAL_SPAN | PZXL-00092-N0054 | PZXL-00092-N0055 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0105 | PHYSICAL_SPAN | PZXL-00092-N0027 | PZXL-00092-N0028 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0106 | PHYSICAL_SPAN | PZXL-00092-N0052 | PZXL-00092-N0053 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0107 | PHYSICAL_SPAN | PZXL-00092-N0164 | PZXL-00092-N0165 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0108 | PHYSICAL_SPAN | PZXL-00092-N0167 | PZXL-00092-N0168 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0109 | PHYSICAL_SPAN | PZXL-00092-N0028 | PZXL-00092-N0029 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0110 | PHYSICAL_SPAN | PZXL-00092-N0057 | PZXL-00092-N0058 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0111 | PHYSICAL_SPAN | PZXL-00092-N0174 | PZXL-00092-N0175 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0112 | PHYSICAL_SPAN | PZXL-00092-N0088 | PZXL-00092-N0089 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0113 | PHYSICAL_SPAN | PZXL-00092-N0119 | PZXL-00092-N0120 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0114 | PHYSICAL_SPAN | PZXL-00092-N0050 | PZXL-00092-N0051 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0115 | PHYSICAL_SPAN | PZXL-00092-N0122 | PZXL-00092-N0123 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0116 | PHYSICAL_SPAN | PZXL-00092-N0185 | PZXL-00092-N0186 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0117 | PHYSICAL_SPAN | PZXL-00092-N0130 | PZXL-00092-N0131 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0118 | PHYSICAL_SPAN | PZXL-00092-N0165 | PZXL-00092-N0166 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0119 | PHYSICAL_SPAN | PZXL-00092-N0207 | PZXL-00092-N0208 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0120 | PHYSICAL_SPAN | PZXL-00092-N0126 | PZXL-00092-N0127 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0121 | PHYSICAL_SPAN | PZXL-00092-N0187 | PZXL-00092-N0188 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0122 | PHYSICAL_SPAN | PZXL-00092-N0095 | PZXL-00092-N0096 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0123 | PHYSICAL_SPAN | PZXL-00092-N0058 | PZXL-00092-N0059 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0124 | PHYSICAL_SPAN | PZXL-00092-N0020 | PZXL-00092-N0021 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0125 | PHYSICAL_SPAN | PZXL-00092-N0056 | PZXL-00092-N0057 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0126 | PHYSICAL_SPAN | PZXL-00092-N0116 | PZXL-00092-N0117 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0127 | PHYSICAL_SPAN | PZXL-00092-N0046 | PZXL-00092-N0047 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0128 | PHYSICAL_SPAN | PZXL-00092-N0102 | PZXL-00092-N0103 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0129 | PHYSICAL_SPAN | PZXL-00092-N0021 | PZXL-00092-N0022 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0130 | PHYSICAL_SPAN | PZXL-00092-N0211 | PZXL-00092-N0212 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0131 | PHYSICAL_SPAN | PZXL-00092-N0103 | PZXL-00092-N0115 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0132 | PHYSICAL_SPAN | PZXL-00092-N0092 | PZXL-00092-N0093 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0133 | PHYSICAL_SPAN | PZXL-00092-N0131 | PZXL-00092-N0132 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0134 | PHYSICAL_SPAN | PZXL-00092-N0212 | PZXL-00092-N0213 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0135 | PHYSICAL_SPAN | PZXL-00092-N0129 | PZXL-00092-N0130 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0136 | PHYSICAL_SPAN | PZXL-00092-N0168 | PZXL-00092-N0169 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0137 | PHYSICAL_SPAN | PZXL-00092-N0193 | PZXL-00092-N0194 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0138 | PHYSICAL_SPAN | PZXL-00092-N0181 | PZXL-00092-N0182 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0139 | PHYSICAL_SPAN | PZXL-00092-N0127 | PZXL-00092-N0128 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0140 | PHYSICAL_SPAN | PZXL-00092-N0194 | PZXL-00092-N0204 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0141 | PHYSICAL_SPAN | PZXL-00092-N0206 | PZXL-00092-N0207 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0142 | PHYSICAL_SPAN | PZXL-00092-N0204 | PZXL-00092-N0205 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0143 | PHYSICAL_SPAN | PZXL-00092-N0120 | PZXL-00092-N0121 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0144 | PHYSICAL_SPAN | PZXL-00092-N0132 | PZXL-00092-N0133 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0145 | PHYSICAL_SPAN | PZXL-00092-N0172 | PZXL-00092-N0173 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0146 | PHYSICAL_SPAN | PZXL-00092-N0128 | PZXL-00092-N0129 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0147 | PHYSICAL_SPAN | PZXL-00092-N0096 | PZXL-00092-N0097 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0148 | PHYSICAL_SPAN | PZXL-00092-N0089 | PZXL-00092-N0090 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0149 | PHYSICAL_SPAN | PZXL-00092-N0192 | PZXL-00092-N0193 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0150 | PHYSICAL_SPAN | PZXL-00092-N0233 | PZXL-00092-N0234 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0151 | PHYSICAL_SPAN | PZXL-00092-N0059 | PZXL-00092-N0060 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0152 | PHYSICAL_SPAN | PZXL-00092-N0100 | PZXL-00092-N0101 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0153 | PHYSICAL_SPAN | PZXL-00092-N0045 | PZXL-00092-N0046 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0154 | PHYSICAL_SPAN | PZXL-00092-N0047 | PZXL-00092-N0048 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0155 | PHYSICAL_SPAN | PZXL-00092-N0117 | PZXL-00092-N0118 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0156 | PHYSICAL_SPAN | PZXL-00092-N0018 | PZXL-00092-N0019 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0157 | PHYSICAL_SPAN | PZXL-00092-N0169 | PZXL-00092-N0170 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0158 | PHYSICAL_SPAN | PZXL-00092-N0017 | PZXL-00092-N0018 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0159 | PHYSICAL_SPAN | PZXL-00092-N0163 | PZXL-00092-N0164 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0160 | PHYSICAL_SPAN | PZXL-00092-N0208 | PZXL-00092-N0209 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0161 | PHYSICAL_SPAN | PZXL-00092-N0173 | PZXL-00092-N0174 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0162 | PHYSICAL_SPAN | PZXL-00092-N0191 | PZXL-00092-N0192 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0163 | PHYSICAL_SPAN | PZXL-00092-N0118 | PZXL-00092-N0119 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0164 | PHYSICAL_SPAN | PZXL-00092-N0097 | PZXL-00092-N0098 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0165 | PHYSICAL_SPAN | PZXL-00092-N0019 | PZXL-00092-N0020 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0166 | PHYSICAL_SPAN | PZXL-00092-N0161 | PZXL-00092-N0162 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0167 | PHYSICAL_SPAN | PZXL-00092-N0053 | PZXL-00092-N0054 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0168 | PHYSICAL_SPAN | PZXL-00092-N0142 | PZXL-00092-N0026 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0169 | PHYSICAL_SPAN | PZXL-00092-N0044 | PZXL-00092-N0045 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0170 | PHYSICAL_SPAN | PZXL-00092-N0188 | PZXL-00092-N0189 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0171 | PHYSICAL_SPAN | PZXL-00092-N0171 | PZXL-00092-N0172 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0172 | PHYSICAL_SPAN | PZXL-00092-N0170 | PZXL-00092-N0171 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0173 | PHYSICAL_SPAN | PZXL-00092-N0215 | PZXL-00092-N0216 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0174 | PHYSICAL_SPAN | PZXL-00092-N0162 | PZXL-00092-N0163 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0175 | PHYSICAL_SPAN | PZXL-00092-N0180 | PZXL-00092-N0181 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0176 | PHYSICAL_SPAN | PZXL-00092-N0189 | PZXL-00092-N0190 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0177 | PHYSICAL_SPAN | PZXL-00092-N0115 | PZXL-00092-N0116 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0178 | PHYSICAL_SPAN | PZXL-00092-N0166 | PZXL-00092-N0167 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0179 | PHYSICAL_SPAN | PZXL-00092-N0051 | PZXL-00092-N0052 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0180 | PHYSICAL_SPAN | PZXL-00092-N0214 | PZXL-00092-N0215 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0181 | PHYSICAL_SPAN | PZXL-00092-N0098 | PZXL-00092-N0099 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0182 | PHYSICAL_SPAN | PZXL-00092-N0121 | PZXL-00092-N0122 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0183 | PHYSICAL_SPAN | PZXL-00092-N0175 | PZXL-00092-N0176 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0184 | PHYSICAL_SPAN | PZXL-00092-N0178 | PZXL-00092-N0179 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0185 | PHYSICAL_SPAN | PZXL-00092-N0099 | PZXL-00092-N0100 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0186 | PHYSICAL_SPAN | PZXL-00092-N0186 | PZXL-00092-N0187 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0187 | PHYSICAL_SPAN | PZXL-00092-N0123 | PZXL-00092-N0125 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0188 | PHYSICAL_SPAN | PZXL-00092-N0160 | PZXL-00092-N0161 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0189 | PHYSICAL_SPAN | PZXL-00092-N0205 | PZXL-00092-N0206 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0190 | PHYSICAL_SPAN | PZXL-00092-N0026 | PZXL-00092-N0027 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0191 | PHYSICAL_SPAN | PZXL-00092-N0190 | PZXL-00092-N0191 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0192 | PHYSICAL_SPAN | PZXL-00092-N0144 | PZXL-00092-N0145 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0193 | PHYSICAL_SPAN | PZXL-00092-N0124 | PZXL-00092-N0007 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0194 | PHYSICAL_SPAN | PZXL-00092-N0007 | PZXL-00092-N0008 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0195 | PHYSICAL_SPAN | PZXL-00092-N0014 | PZXL-00092-N0015 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0196 | PHYSICAL_SPAN | PZXL-00092-N0265 | PZXL-00092-N0266 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0197 | PHYSICAL_SPAN | PZXL-00092-N0012 | PZXL-00092-N0013 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0198 | PHYSICAL_SPAN | PZXL-00092-N0010 | PZXL-00092-N0011 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0199 | PHYSICAL_SPAN | PZXL-00092-N0011 | PZXL-00092-N0012 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0200 | PHYSICAL_SPAN | PZXL-00092-N0125 | PZXL-00092-N0124 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0201 | PHYSICAL_SPAN | PZXL-00092-N0264 | PZXL-00092-N0265 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0202 | PHYSICAL_SPAN | PZXL-00092-N0013 | PZXL-00092-N0014 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0203 | PHYSICAL_SPAN | PZXL-00092-N0145 | PZXL-00092-N0146 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0204 | PHYSICAL_SPAN | PZXL-00092-N0124 | PZXL-00092-N0126 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0205 | PHYSICAL_SPAN | PZXL-00092-N0008 | PZXL-00092-N0009 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0206 | PHYSICAL_SPAN | PZXL-00092-N0041 | PZXL-00092-N0263 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0207 | PHYSICAL_SPAN | PZXL-00092-N0009 | PZXL-00092-N0010 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0208 | PHYSICAL_SPAN | PZXL-00092-N0109 | PZXL-00092-N0110 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0209 | PHYSICAL_SPAN | PZXL-00092-N0111 | PZXL-00092-N0112 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0210 | PHYSICAL_SPAN | PZXL-00092-N0108 | PZXL-00092-N0109 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0211 | PHYSICAL_SPAN | PZXL-00092-N0112 | PZXL-00092-N0113 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0212 | PHYSICAL_SPAN | PZXL-00092-N0104 | PZXL-00092-N0107 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0213 | PHYSICAL_SPAN | PZXL-00092-N0105 | PZXL-00092-N0106 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0214 | PHYSICAL_SPAN | PZXL-00092-N0115 | PZXL-00092-N0104 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0215 | PHYSICAL_SPAN | PZXL-00092-N0110 | PZXL-00092-N0111 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0216 | PHYSICAL_SPAN | PZXL-00092-N0113 | PZXL-00092-N0114 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0217 | PHYSICAL_SPAN | PZXL-00092-N0114 | PZXL-00092-N0105 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0218 | PHYSICAL_SPAN | PZXL-00092-N0107 | PZXL-00092-N0108 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0219 | PHYSICAL_SPAN | PZXL-00092-N0156 | PZXL-00092-N0157 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0220 | PHYSICAL_SPAN | PZXL-00092-N0155 | PZXL-00092-N0268 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0221 | PHYSICAL_SPAN | PZXL-00092-N0158 | PZXL-00092-N0159 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0222 | PHYSICAL_SPAN | PZXL-00092-N0155 | PZXL-00092-N0156 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0223 | PHYSICAL_SPAN | PZXL-00092-N0268 | PZXL-00092-N0269 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0224 | PHYSICAL_SPAN | PZXL-00092-N0157 | PZXL-00092-N0158 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0225 | PHYSICAL_SPAN | PZXL-00092-N0198 | PZXL-00092-N0199 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0226 | PHYSICAL_SPAN | PZXL-00092-N0195 | PZXL-00092-N0196 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0227 | PHYSICAL_SPAN | PZXL-00092-N0202 | PZXL-00092-N0203 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0228 | PHYSICAL_SPAN | PZXL-00092-N0256 | PZXL-00092-N0257 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0229 | PHYSICAL_SPAN | PZXL-00092-N0200 | PZXL-00092-N0201 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0230 | PHYSICAL_SPAN | PZXL-00092-N0194 | PZXL-00092-N0195 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0231 | PHYSICAL_SPAN | PZXL-00092-N0199 | PZXL-00092-N0200 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0232 | PHYSICAL_SPAN | PZXL-00092-N0253 | PZXL-00092-N0254 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0233 | PHYSICAL_SPAN | PZXL-00092-N0046 | PZXL-00092-N0253 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0234 | PHYSICAL_SPAN | PZXL-00092-N0201 | PZXL-00092-N0202 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0235 | PHYSICAL_SPAN | PZXL-00092-N0255 | PZXL-00092-N0256 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0236 | PHYSICAL_SPAN | PZXL-00092-N0196 | PZXL-00092-N0197 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0237 | PHYSICAL_SPAN | PZXL-00092-N0254 | PZXL-00092-N0255 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0238 | PHYSICAL_SPAN | PZXL-00092-N0197 | PZXL-00092-N0198 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0239 | PHYSICAL_SPAN | PZXL-00092-N0068 | PZXL-00092-N0066 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0240 | PHYSICAL_SPAN | PZXL-00092-N0242 | PZXL-00092-N0251 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0241 | PHYSICAL_SPAN | PZXL-00092-N0066 | PZXL-00092-N0067 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0242 | PHYSICAL_SPAN | PZXL-00092-N0237 | PZXL-00092-N0238 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0243 | PHYSICAL_SPAN | PZXL-00092-N0259 | PZXL-00092-N0260 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0244 | PHYSICAL_SPAN | PZXL-00092-N0240 | PZXL-00092-N0241 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0245 | PHYSICAL_SPAN | PZXL-00092-N0258 | PZXL-00092-N0259 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0246 | PHYSICAL_SPAN | PZXL-00092-N0085 | PZXL-00092-N0086 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0247 | PHYSICAL_SPAN | PZXL-00092-N0087 | PZXL-00092-N0085 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0248 | PHYSICAL_SPAN | PZXL-00092-N0095 | PZXL-00092-N0258 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0249 | PHYSICAL_SPAN | PZXL-00092-N0260 | PZXL-00092-N0261 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0250 | PHYSICAL_SPAN | PZXL-00092-N0247 | PZXL-00092-N0248 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0251 | PHYSICAL_SPAN | PZXL-00092-N0248 | PZXL-00092-N0249 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0252 | PHYSICAL_SPAN | PZXL-00092-N0249 | PZXL-00092-N0250 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0253 | PHYSICAL_SPAN | PZXL-00092-N0245 | PZXL-00092-N0246 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0254 | PHYSICAL_SPAN | PZXL-00092-N0246 | PZXL-00092-N0247 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0255 | PHYSICAL_SPAN | PZXL-00092-N0244 | PZXL-00092-N0245 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0256 | PHYSICAL_SPAN | PZXL-00092-N0243 | PZXL-00092-N0244 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0257 | PHYSICAL_SPAN | PZXL-00092-N0239 | PZXL-00092-N0240 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0258 | PHYSICAL_SPAN | PZXL-00092-N0236 | PZXL-00092-N0237 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0259 | PHYSICAL_SPAN | PZXL-00092-N0238 | PZXL-00092-N0239 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0260 | PHYSICAL_SPAN | PZXL-00092-N0075 | PZXL-00092-N0076 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0261 | PHYSICAL_SPAN | PZXL-00092-N0076 | PZXL-00092-N0077 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0262 | PHYSICAL_SPAN | PZXL-00092-N0079 | PZXL-00092-N0080 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0263 | PHYSICAL_SPAN | PZXL-00092-N0082 | PZXL-00092-N0075 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0264 | PHYSICAL_SPAN | PZXL-00092-N0077 | PZXL-00092-N0078 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0265 | PHYSICAL_SPAN | PZXL-00092-N0080 | PZXL-00092-N0081 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0266 | PHYSICAL_SPAN | PZXL-00092-N0078 | PZXL-00092-N0079 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00092-B0267 | PHYSICAL_SPAN | PZXL-00092-N0266 | PZXL-00092-N0267 | PZXL-00092 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kVdnan线明细.xlsx
PZXL-00099-B0001 | PHYSICAL_SPAN | PZXL-00099-N0056 | PZXL-00099-N0057 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0002 | PHYSICAL_SPAN | PZXL-00099-N0156 | PZXL-00099-N0160 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0003 | PHYSICAL_SPAN | PZXL-00099-N0154 | PZXL-00099-N0155 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0004 | PHYSICAL_SPAN | PZXL-00099-N0158 | PZXL-00099-N0159 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0005 | PHYSICAL_SPAN | PZXL-00099-N0155 | PZXL-00099-N0157 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0006 | PHYSICAL_SPAN | PZXL-00099-N0153 | PZXL-00099-N0154 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0007 | PHYSICAL_SPAN | PZXL-00099-N0157 | PZXL-00099-N0158 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0008 | PHYSICAL_SPAN | PZXL-00099-N0150 | PZXL-00099-N0151 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0009 | PHYSICAL_SPAN | PZXL-00099-N0140 | PZXL-00099-N0141 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0010 | PHYSICAL_SPAN | PZXL-00099-N0130 | PZXL-00099-N0131 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0011 | PHYSICAL_SPAN | PZXL-00099-N0152 | PZXL-00099-N0153 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0012 | PHYSICAL_SPAN | PZXL-00099-N0145 | PZXL-00099-N0124 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0013 | PHYSICAL_SPAN | PZXL-00099-N0121 | PZXL-00099-N0122 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0014 | PHYSICAL_SPAN | PZXL-00099-N0114 | PZXL-00099-N0115 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0015 | PHYSICAL_SPAN | PZXL-00099-N0108 | PZXL-00099-N0109 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0016 | PHYSICAL_SPAN | PZXL-00099-N0131 | PZXL-00099-N0132 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0017 | PHYSICAL_SPAN | PZXL-00099-N0086 | PZXL-00099-N0087 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0018 | PHYSICAL_SPAN | PZXL-00099-N0104 | PZXL-00099-N0105 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0019 | PHYSICAL_SPAN | PZXL-00099-N0079 | PZXL-00099-N0080 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0020 | PHYSICAL_SPAN | PZXL-00099-N0095 | PZXL-00099-N0097 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0021 | PHYSICAL_SPAN | PZXL-00099-N0098 | PZXL-00099-N0099 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0022 | PHYSICAL_SPAN | PZXL-00099-N0059 | PZXL-00099-N0060 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0023 | PHYSICAL_SPAN | PZXL-00099-N0133 | PZXL-00099-N0116 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0024 | PHYSICAL_SPAN | PZXL-00099-N0149 | PZXL-00099-N0150 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0025 | PHYSICAL_SPAN | PZXL-00099-N0163 | PZXL-00099-N0164 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0026 | PHYSICAL_SPAN | PZXL-00099-N0127 | PZXL-00099-N0128 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0027 | PHYSICAL_SPAN | PZXL-00099-N0109 | PZXL-00099-N0110 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0028 | PHYSICAL_SPAN | PZXL-00099-N0115 | PZXL-00099-N0092 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0029 | PHYSICAL_SPAN | PZXL-00099-N0161 | PZXL-00099-N0162 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0030 | PHYSICAL_SPAN | PZXL-00099-N0099 | PZXL-00099-N0100 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0031 | PHYSICAL_SPAN | PZXL-00099-N0122 | PZXL-00099-N0123 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0032 | PHYSICAL_SPAN | PZXL-00099-N0100 | PZXL-00099-N0101 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0033 | PHYSICAL_SPAN | PZXL-00099-N0096 | PZXL-00099-N0156 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0034 | PHYSICAL_SPAN | PZXL-00099-N0096 | PZXL-00099-N0095 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0035 | PHYSICAL_SPAN | PZXL-00099-N0151 | PZXL-00099-N0152 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0036 | PHYSICAL_SPAN | PZXL-00099-N0113 | PZXL-00099-N0077 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0037 | PHYSICAL_SPAN | PZXL-00099-N0078 | PZXL-00099-N0079 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0038 | PHYSICAL_SPAN | PZXL-00099-N0128 | PZXL-00099-N0129 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0039 | PHYSICAL_SPAN | PZXL-00099-N0077 | PZXL-00099-N0078 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0040 | PHYSICAL_SPAN | PZXL-00099-N0105 | PZXL-00099-N0106 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0041 | PHYSICAL_SPAN | PZXL-00099-N0106 | PZXL-00099-N0107 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0042 | PHYSICAL_SPAN | PZXL-00099-N0143 | PZXL-00099-N0144 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0043 | PHYSICAL_SPAN | PZXL-00099-N0015 | PZXL-00099-N0016 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0044 | PHYSICAL_SPAN | PZXL-00099-N0024 | PZXL-00099-N0025 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0045 | PHYSICAL_SPAN | PZXL-00099-N0001 | PZXL-00099-N0002 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0046 | PHYSICAL_SPAN | PZXL-00099-N0006 | PZXL-00099-N0051 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0047 | PHYSICAL_SPAN | PZXL-00099-N0065 | PZXL-00099-N0066 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0048 | PHYSICAL_SPAN | PZXL-00099-N0015 | PZXL-00099-N0120 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0049 | PHYSICAL_SPAN | PZXL-00099-N0167 | PZXL-00099-N0146 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0050 | PHYSICAL_SPAN | PZXL-00099-N0160 | PZXL-00099-N0161 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0051 | PHYSICAL_SPAN | PZXL-00099-N0166 | PZXL-00099-N0167 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0052 | PHYSICAL_SPAN | PZXL-00099-N0147 | PZXL-00099-N0148 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0053 | PHYSICAL_SPAN | PZXL-00099-N0126 | PZXL-00099-N0127 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0054 | PHYSICAL_SPAN | PZXL-00099-N0093 | PZXL-00099-N0094 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0055 | PHYSICAL_SPAN | PZXL-00099-N0102 | PZXL-00099-N0104 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0056 | PHYSICAL_SPAN | PZXL-00099-N0113 | PZXL-00099-N0114 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0057 | PHYSICAL_SPAN | PZXL-00099-N0162 | PZXL-00099-N0163 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0058 | PHYSICAL_SPAN | PZXL-00099-N0146 | PZXL-00099-N0147 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0059 | PHYSICAL_SPAN | PZXL-00099-N0112 | PZXL-00099-N0113 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0060 | PHYSICAL_SPAN | PZXL-00099-N0133 | PZXL-00099-N0135 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0061 | PHYSICAL_SPAN | PZXL-00099-N0139 | PZXL-00099-N0140 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0062 | PHYSICAL_SPAN | PZXL-00099-N0083 | PZXL-00099-N0084 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0063 | PHYSICAL_SPAN | PZXL-00099-N0134 | PZXL-00099-N0138 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0064 | PHYSICAL_SPAN | PZXL-00099-N0136 | PZXL-00099-N0137 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0065 | PHYSICAL_SPAN | PZXL-00099-N0118 | PZXL-00099-N0119 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0066 | PHYSICAL_SPAN | PZXL-00099-N0042 | PZXL-00099-N0043 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0067 | PHYSICAL_SPAN | PZXL-00099-N0045 | PZXL-00099-N0046 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0068 | PHYSICAL_SPAN | PZXL-00099-N0125 | PZXL-00099-N0126 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0069 | PHYSICAL_SPAN | PZXL-00099-N0148 | PZXL-00099-N0149 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0070 | PHYSICAL_SPAN | PZXL-00099-N0129 | PZXL-00099-N0130 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0071 | PHYSICAL_SPAN | PZXL-00099-N0043 | PZXL-00099-N0044 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0072 | PHYSICAL_SPAN | PZXL-00099-N0141 | PZXL-00099-N0142 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0073 | PHYSICAL_SPAN | PZXL-00099-N0124 | PZXL-00099-N0125 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0074 | PHYSICAL_SPAN | PZXL-00099-N0080 | PZXL-00099-N0081 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0075 | PHYSICAL_SPAN | PZXL-00099-N0138 | PZXL-00099-N0139 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0076 | PHYSICAL_SPAN | PZXL-00099-N0110 | PZXL-00099-N0111 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0077 | PHYSICAL_SPAN | PZXL-00099-N0092 | PZXL-00099-N0093 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0078 | PHYSICAL_SPAN | PZXL-00099-N0164 | PZXL-00099-N0165 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0079 | PHYSICAL_SPAN | PZXL-00099-N0142 | PZXL-00099-N0143 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0080 | PHYSICAL_SPAN | PZXL-00099-N0144 | PZXL-00099-N0145 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0081 | PHYSICAL_SPAN | PZXL-00099-N0116 | PZXL-00099-N0117 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0082 | PHYSICAL_SPAN | PZXL-00099-N0094 | PZXL-00099-N0096 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0083 | PHYSICAL_SPAN | PZXL-00099-N0044 | PZXL-00099-N0045 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0084 | PHYSICAL_SPAN | PZXL-00099-N0132 | PZXL-00099-N0133 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0085 | PHYSICAL_SPAN | PZXL-00099-N0084 | PZXL-00099-N0085 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0086 | PHYSICAL_SPAN | PZXL-00099-N0135 | PZXL-00099-N0136 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0087 | PHYSICAL_SPAN | PZXL-00099-N0111 | PZXL-00099-N0112 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0088 | PHYSICAL_SPAN | PZXL-00099-N0058 | PZXL-00099-N0059 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0089 | PHYSICAL_SPAN | PZXL-00099-N0101 | PZXL-00099-N0102 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0090 | PHYSICAL_SPAN | PZXL-00099-N0103 | PZXL-00099-N0108 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0091 | PHYSICAL_SPAN | PZXL-00099-N0165 | PZXL-00099-N0166 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0092 | PHYSICAL_SPAN | PZXL-00099-N0120 | PZXL-00099-N0121 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0093 | PHYSICAL_SPAN | PZXL-00099-N0085 | PZXL-00099-N0086 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0094 | PHYSICAL_SPAN | PZXL-00099-N0063 | PZXL-00099-N0064 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0095 | PHYSICAL_SPAN | PZXL-00099-N0066 | PZXL-00099-N0067 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0096 | PHYSICAL_SPAN | PZXL-00099-N0031 | PZXL-00099-N0032 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0097 | PHYSICAL_SPAN | PZXL-00099-N0034 | PZXL-00099-N0035 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0098 | PHYSICAL_SPAN | PZXL-00099-N0011 | PZXL-00099-N0012 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0099 | PHYSICAL_SPAN | PZXL-00099-N0074 | PZXL-00099-N0075 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0100 | PHYSICAL_SPAN | PZXL-00099-N0051 | PZXL-00099-N0052 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0101 | PHYSICAL_SPAN | PZXL-00099-N0019 | PZXL-00099-N0020 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0102 | PHYSICAL_SPAN | PZXL-00099-N0036 | PZXL-00099-N0037 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0103 | PHYSICAL_SPAN | PZXL-00099-N0032 | PZXL-00099-N0033 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0104 | PHYSICAL_SPAN | PZXL-00099-N0020 | PZXL-00099-N0021 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0105 | PHYSICAL_SPAN | PZXL-00099-N0039 | PZXL-00099-N0040 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0106 | PHYSICAL_SPAN | PZXL-00099-N0037 | PZXL-00099-N0038 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0107 | PHYSICAL_SPAN | PZXL-00099-N0009 | PZXL-00099-N0010 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0108 | PHYSICAL_SPAN | PZXL-00099-N0070 | PZXL-00099-N0071 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0109 | PHYSICAL_SPAN | PZXL-00099-N0062 | PZXL-00099-N0063 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0110 | PHYSICAL_SPAN | PZXL-00099-N0038 | PZXL-00099-N0039 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0111 | PHYSICAL_SPAN | PZXL-00099-N0035 | PZXL-00099-N0036 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0112 | PHYSICAL_SPAN | PZXL-00099-N0004 | PZXL-00099-N0005 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0113 | PHYSICAL_SPAN | PZXL-00099-N0023 | PZXL-00099-N0024 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0114 | PHYSICAL_SPAN | PZXL-00099-N0008 | PZXL-00099-N0009 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0115 | PHYSICAL_SPAN | PZXL-00099-N0040 | PZXL-00099-N0041 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0116 | PHYSICAL_SPAN | PZXL-00099-N0053 | PZXL-00099-N0054 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0117 | PHYSICAL_SPAN | PZXL-00099-N0073 | PZXL-00099-N0074 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0118 | PHYSICAL_SPAN | PZXL-00099-N0072 | PZXL-00099-N0073 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0119 | PHYSICAL_SPAN | PZXL-00099-N0021 | PZXL-00099-N0022 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0120 | PHYSICAL_SPAN | PZXL-00099-N0030 | PZXL-00099-N0031 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0121 | PHYSICAL_SPAN | PZXL-00099-N0018 | PZXL-00099-N0019 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0122 | PHYSICAL_SPAN | PZXL-00099-N0005 | PZXL-00099-N0006 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0123 | PHYSICAL_SPAN | PZXL-00099-N0002 | PZXL-00099-N0003 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0124 | PHYSICAL_SPAN | PZXL-00099-N0054 | PZXL-00099-N0055 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0125 | PHYSICAL_SPAN | PZXL-00099-N0003 | PZXL-00099-N0004 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0126 | PHYSICAL_SPAN | PZXL-00099-N0026 | PZXL-00099-N0027 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0127 | PHYSICAL_SPAN | PZXL-00099-N0016 | PZXL-00099-N0017 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0128 | PHYSICAL_SPAN | PZXL-00099-N0014 | PZXL-00099-N0015 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0129 | PHYSICAL_SPAN | PZXL-00099-N0022 | PZXL-00099-N0023 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0130 | PHYSICAL_SPAN | PZXL-00099-N0069 | PZXL-00099-N0070 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0131 | PHYSICAL_SPAN | PZXL-00099-N0017 | PZXL-00099-N0018 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0132 | PHYSICAL_SPAN | PZXL-00099-N0067 | PZXL-00099-N0068 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0133 | PHYSICAL_SPAN | PZXL-00099-N0010 | PZXL-00099-N0011 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0134 | PHYSICAL_SPAN | PZXL-00099-N0071 | PZXL-00099-N0072 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0135 | PHYSICAL_SPAN | PZXL-00099-N0076 | PZXL-00099-N0061 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0136 | PHYSICAL_SPAN | PZXL-00099-N0061 | PZXL-00099-N0062 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0137 | PHYSICAL_SPAN | PZXL-00099-N0033 | PZXL-00099-N0034 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0138 | PHYSICAL_SPAN | PZXL-00099-N0025 | PZXL-00099-N0026 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0139 | PHYSICAL_SPAN | PZXL-00099-N0028 | PZXL-00099-N0030 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0140 | PHYSICAL_SPAN | PZXL-00099-N0075 | PZXL-00099-N0076 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0141 | PHYSICAL_SPAN | PZXL-00099-N0064 | PZXL-00099-N0065 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0142 | PHYSICAL_SPAN | PZXL-00099-N0012 | PZXL-00099-N0013 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0143 | PHYSICAL_SPAN | PZXL-00099-N0052 | PZXL-00099-N0053 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0144 | PHYSICAL_SPAN | PZXL-00099-N0027 | PZXL-00099-N0028 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0145 | PHYSICAL_SPAN | PZXL-00099-N0041 | PZXL-00099-N0042 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0146 | PHYSICAL_SPAN | PZXL-00099-N0013 | PZXL-00099-N0014 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0147 | PHYSICAL_SPAN | PZXL-00099-N0049 | PZXL-00099-N0050 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0148 | PHYSICAL_SPAN | PZXL-00099-N0110 | PZXL-00099-N0047 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0149 | PHYSICAL_SPAN | PZXL-00099-N0047 | PZXL-00099-N0048 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0150 | PHYSICAL_SPAN | PZXL-00099-N0048 | PZXL-00099-N0049 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0151 | PHYSICAL_SPAN | PZXL-00099-N0061 | PZXL-00099-N0083 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0152 | PHYSICAL_SPAN | PZXL-00099-N0034 | PZXL-00099-N0118 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ-240/10 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0153 | PHYSICAL_SPAN | PZXL-00099-N0015 | PZXL-00099-N0134 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ-240/10 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0154 | PHYSICAL_SPAN | PZXL-00099-N0006 | PZXL-00099-N0007 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLGYJ-70 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0155 | PHYSICAL_SPAN | PZXL-00099-N0097 | PZXL-00099-N0098 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ-240/10 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0156 | PHYSICAL_SPAN | PZXL-00099-N0090 | PZXL-00099-N0091 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0157 | PHYSICAL_SPAN | PZXL-00099-N0088 | PZXL-00099-N0089 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0158 | PHYSICAL_SPAN | PZXL-00099-N0091 | PZXL-00099-N0082 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0159 | PHYSICAL_SPAN | PZXL-00099-N0089 | PZXL-00099-N0090 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0160 | PHYSICAL_SPAN | PZXL-00099-N0087 | PZXL-00099-N0088 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00099-B0161 | PHYSICAL_SPAN | PZXL-00099-N0030 | PZXL-00099-N0029 | PZXL-00099 | CLOSED | CLOSED | YES | 50 | JLRX/T-120/30 | R_X_IMAX_PENDING | 邳州_10kV墩振线明细.xlsx
PZXL-00097-B0001 | PHYSICAL_SPAN | PZXL-00097-N0191 | PZXL-00097-N0192 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0002 | PHYSICAL_SPAN | PZXL-00097-N0189 | PZXL-00097-N0190 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0003 | PHYSICAL_SPAN | PZXL-00097-N0180 | PZXL-00097-N0188 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0004 | PHYSICAL_SPAN | PZXL-00097-N0190 | PZXL-00097-N0191 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0005 | PHYSICAL_SPAN | PZXL-00097-N0188 | PZXL-00097-N0189 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0006 | PHYSICAL_SPAN | PZXL-00097-N0089 | PZXL-00097-N0088 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0007 | PHYSICAL_SPAN | PZXL-00097-N0049 | PZXL-00097-N0050 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0008 | PHYSICAL_SPAN | PZXL-00097-N0182 | PZXL-00097-N0193 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0009 | PHYSICAL_SPAN | PZXL-00097-N0160 | PZXL-00097-N0107 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0010 | PHYSICAL_SPAN | PZXL-00097-N0170 | PZXL-00097-N0171 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0011 | PHYSICAL_SPAN | PZXL-00097-N0108 | PZXL-00097-N0109 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0012 | PHYSICAL_SPAN | PZXL-00097-N0172 | PZXL-00097-N0173 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0013 | PHYSICAL_SPAN | PZXL-00097-N0169 | PZXL-00097-N0170 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0014 | PHYSICAL_SPAN | PZXL-00097-N0109 | PZXL-00097-N0110 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0015 | PHYSICAL_SPAN | PZXL-00097-N0049 | PZXL-00097-N0011 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0016 | PHYSICAL_SPAN | PZXL-00097-N0171 | PZXL-00097-N0172 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0017 | PHYSICAL_SPAN | PZXL-00097-N0107 | PZXL-00097-N0108 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0018 | PHYSICAL_SPAN | PZXL-00097-N0166 | PZXL-00097-N0174 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0019 | PHYSICAL_SPAN | PZXL-00097-N0052 | PZXL-00097-N0053 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0020 | PHYSICAL_SPAN | PZXL-00097-N0058 | PZXL-00097-N0059 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0021 | PHYSICAL_SPAN | PZXL-00097-N0051 | PZXL-00097-N0052 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0022 | PHYSICAL_SPAN | PZXL-00097-N0057 | PZXL-00097-N0058 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0023 | PHYSICAL_SPAN | PZXL-00097-N0043 | PZXL-00097-N0001 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0024 | PHYSICAL_SPAN | PZXL-00097-N0064 | PZXL-00097-N0065 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0025 | PHYSICAL_SPAN | PZXL-00097-N0055 | PZXL-00097-N0057 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0026 | PHYSICAL_SPAN | PZXL-00097-N0042 | PZXL-00097-N0043 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0027 | PHYSICAL_SPAN | PZXL-00097-N0033 | PZXL-00097-N0038 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0028 | PHYSICAL_SPAN | PZXL-00097-N0060 | PZXL-00097-N0061 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0029 | PHYSICAL_SPAN | PZXL-00097-N0053 | PZXL-00097-N0054 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0030 | PHYSICAL_SPAN | PZXL-00097-N0046 | PZXL-00097-N0047 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0031 | PHYSICAL_SPAN | PZXL-00097-N0054 | PZXL-00097-N0055 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0032 | PHYSICAL_SPAN | PZXL-00097-N0140 | PZXL-00097-N0141 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0033 | PHYSICAL_SPAN | PZXL-00097-N0143 | PZXL-00097-N0144 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0034 | PHYSICAL_SPAN | PZXL-00097-N0174 | PZXL-00097-N0175 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0035 | PHYSICAL_SPAN | PZXL-00097-N0176 | PZXL-00097-N0177 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0036 | PHYSICAL_SPAN | PZXL-00097-N0179 | PZXL-00097-N0180 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0037 | PHYSICAL_SPAN | PZXL-00097-N0185 | PZXL-00097-N0186 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0038 | PHYSICAL_SPAN | PZXL-00097-N0184 | PZXL-00097-N0185 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0039 | PHYSICAL_SPAN | PZXL-00097-N0160 | PZXL-00097-N0161 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0040 | PHYSICAL_SPAN | PZXL-00097-N0166 | PZXL-00097-N0167 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0041 | PHYSICAL_SPAN | PZXL-00097-N0134 | PZXL-00097-N0135 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0042 | PHYSICAL_SPAN | PZXL-00097-N0145 | PZXL-00097-N0146 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0043 | PHYSICAL_SPAN | PZXL-00097-N0165 | PZXL-00097-N0166 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0044 | PHYSICAL_SPAN | PZXL-00097-N0168 | PZXL-00097-N0169 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0045 | PHYSICAL_SPAN | PZXL-00097-N0070 | PZXL-00097-N0071 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0046 | PHYSICAL_SPAN | PZXL-00097-N0002 | PZXL-00097-N0003 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0047 | PHYSICAL_SPAN | PZXL-00097-N0005 | PZXL-00097-N0006 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0048 | PHYSICAL_SPAN | PZXL-00097-N0016 | PZXL-00097-N0017 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0049 | PHYSICAL_SPAN | PZXL-00097-N0078 | PZXL-00097-N0079 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0050 | PHYSICAL_SPAN | PZXL-00097-N0021 | PZXL-00097-N0023 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0051 | PHYSICAL_SPAN | PZXL-00097-N0010 | PZXL-00097-N0012 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0052 | PHYSICAL_SPAN | PZXL-00097-N0130 | PZXL-00097-N0131 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0053 | PHYSICAL_SPAN | PZXL-00097-N0075 | PZXL-00097-N0076 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0054 | PHYSICAL_SPAN | PZXL-00097-N0082 | PZXL-00097-N0083 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0055 | PHYSICAL_SPAN | PZXL-00097-N0027 | PZXL-00097-N0028 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0056 | PHYSICAL_SPAN | PZXL-00097-N0029 | PZXL-00097-N0030 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0057 | PHYSICAL_SPAN | PZXL-00097-N0020 | PZXL-00097-N0021 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0058 | PHYSICAL_SPAN | PZXL-00097-N0026 | PZXL-00097-N0027 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0059 | PHYSICAL_SPAN | PZXL-00097-N0031 | PZXL-00097-N0032 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0060 | PHYSICAL_SPAN | PZXL-00097-N0163 | PZXL-00097-N0164 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0061 | PHYSICAL_SPAN | PZXL-00097-N0182 | PZXL-00097-N0183 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0062 | PHYSICAL_SPAN | PZXL-00097-N0139 | PZXL-00097-N0140 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0063 | PHYSICAL_SPAN | PZXL-00097-N0186 | PZXL-00097-N0187 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0064 | PHYSICAL_SPAN | PZXL-00097-N0149 | PZXL-00097-N0150 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0065 | PHYSICAL_SPAN | PZXL-00097-N0157 | PZXL-00097-N0158 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0066 | PHYSICAL_SPAN | PZXL-00097-N0024 | PZXL-00097-N0025 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0067 | PHYSICAL_SPAN | PZXL-00097-N0161 | PZXL-00097-N0162 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0068 | PHYSICAL_SPAN | PZXL-00097-N0162 | PZXL-00097-N0163 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0069 | PHYSICAL_SPAN | PZXL-00097-N0007 | PZXL-00097-N0008 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0070 | PHYSICAL_SPAN | PZXL-00097-N0074 | PZXL-00097-N0075 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0071 | PHYSICAL_SPAN | PZXL-00097-N0076 | PZXL-00097-N0077 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0072 | PHYSICAL_SPAN | PZXL-00097-N0183 | PZXL-00097-N0184 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0073 | PHYSICAL_SPAN | PZXL-00097-N0177 | PZXL-00097-N0178 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0074 | PHYSICAL_SPAN | PZXL-00097-N0153 | PZXL-00097-N0154 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0075 | PHYSICAL_SPAN | PZXL-00097-N0137 | PZXL-00097-N0138 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0076 | PHYSICAL_SPAN | PZXL-00097-N0141 | PZXL-00097-N0142 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0077 | PHYSICAL_SPAN | PZXL-00097-N0146 | PZXL-00097-N0147 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0078 | PHYSICAL_SPAN | PZXL-00097-N0008 | PZXL-00097-N0009 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0079 | PHYSICAL_SPAN | PZXL-00097-N0017 | PZXL-00097-N0018 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0080 | PHYSICAL_SPAN | PZXL-00097-N0073 | PZXL-00097-N0074 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0081 | PHYSICAL_SPAN | PZXL-00097-N0083 | PZXL-00097-N0084 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0082 | PHYSICAL_SPAN | PZXL-00097-N0018 | PZXL-00097-N0019 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0083 | PHYSICAL_SPAN | PZXL-00097-N0059 | PZXL-00097-N0130 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0084 | PHYSICAL_SPAN | PZXL-00097-N0132 | PZXL-00097-N0133 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0085 | PHYSICAL_SPAN | PZXL-00097-N0036 | PZXL-00097-N0037 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0086 | PHYSICAL_SPAN | PZXL-00097-N0014 | PZXL-00097-N0015 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0087 | PHYSICAL_SPAN | PZXL-00097-N0015 | PZXL-00097-N0016 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0088 | PHYSICAL_SPAN | PZXL-00097-N0180 | PZXL-00097-N0181 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0089 | PHYSICAL_SPAN | PZXL-00097-N0079 | PZXL-00097-N0080 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0090 | PHYSICAL_SPAN | PZXL-00097-N0081 | PZXL-00097-N0082 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0091 | PHYSICAL_SPAN | PZXL-00097-N0023 | PZXL-00097-N0024 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0092 | PHYSICAL_SPAN | PZXL-00097-N0167 | PZXL-00097-N0168 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0093 | PHYSICAL_SPAN | PZXL-00097-N0131 | PZXL-00097-N0132 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0094 | PHYSICAL_SPAN | PZXL-00097-N0136 | PZXL-00097-N0137 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0095 | PHYSICAL_SPAN | PZXL-00097-N0156 | PZXL-00097-N0157 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0096 | PHYSICAL_SPAN | PZXL-00097-N0158 | PZXL-00097-N0159 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0097 | PHYSICAL_SPAN | PZXL-00097-N0013 | PZXL-00097-N0014 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0098 | PHYSICAL_SPAN | PZXL-00097-N0133 | PZXL-00097-N0134 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0099 | PHYSICAL_SPAN | PZXL-00097-N0155 | PZXL-00097-N0156 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0100 | PHYSICAL_SPAN | PZXL-00097-N0085 | PZXL-00097-N0086 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0101 | PHYSICAL_SPAN | PZXL-00097-N0039 | PZXL-00097-N0040 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0102 | PHYSICAL_SPAN | PZXL-00097-N0044 | PZXL-00097-N0045 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0103 | PHYSICAL_SPAN | PZXL-00097-N0175 | PZXL-00097-N0176 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0104 | PHYSICAL_SPAN | PZXL-00097-N0138 | PZXL-00097-N0139 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0105 | PHYSICAL_SPAN | PZXL-00097-N0142 | PZXL-00097-N0143 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0106 | PHYSICAL_SPAN | PZXL-00097-N0148 | PZXL-00097-N0149 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0107 | PHYSICAL_SPAN | PZXL-00097-N0164 | PZXL-00097-N0165 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0108 | PHYSICAL_SPAN | PZXL-00097-N0152 | PZXL-00097-N0153 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0109 | PHYSICAL_SPAN | PZXL-00097-N0009 | PZXL-00097-N0010 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0110 | PHYSICAL_SPAN | PZXL-00097-N0025 | PZXL-00097-N0026 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0111 | PHYSICAL_SPAN | PZXL-00097-N0077 | PZXL-00097-N0078 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0112 | PHYSICAL_SPAN | PZXL-00097-N0080 | PZXL-00097-N0081 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0113 | PHYSICAL_SPAN | PZXL-00097-N0012 | PZXL-00097-N0013 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0114 | PHYSICAL_SPAN | PZXL-00097-N0019 | PZXL-00097-N0020 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0115 | PHYSICAL_SPAN | PZXL-00097-N0028 | PZXL-00097-N0029 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0116 | PHYSICAL_SPAN | PZXL-00097-N0071 | PZXL-00097-N0072 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0117 | PHYSICAL_SPAN | PZXL-00097-N0003 | PZXL-00097-N0004 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0118 | PHYSICAL_SPAN | PZXL-00097-N0030 | PZXL-00097-N0031 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0119 | PHYSICAL_SPAN | PZXL-00097-N0084 | PZXL-00097-N0085 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0120 | PHYSICAL_SPAN | PZXL-00097-N0004 | PZXL-00097-N0005 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0121 | PHYSICAL_SPAN | PZXL-00097-N0181 | PZXL-00097-N0182 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0122 | PHYSICAL_SPAN | PZXL-00097-N0147 | PZXL-00097-N0148 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0123 | PHYSICAL_SPAN | PZXL-00097-N0154 | PZXL-00097-N0155 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0124 | PHYSICAL_SPAN | PZXL-00097-N0150 | PZXL-00097-N0151 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0125 | PHYSICAL_SPAN | PZXL-00097-N0151 | PZXL-00097-N0152 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0126 | PHYSICAL_SPAN | PZXL-00097-N0144 | PZXL-00097-N0145 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0127 | PHYSICAL_SPAN | PZXL-00097-N0159 | PZXL-00097-N0160 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0128 | PHYSICAL_SPAN | PZXL-00097-N0069 | PZXL-00097-N0070 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0129 | PHYSICAL_SPAN | PZXL-00097-N0032 | PZXL-00097-N0034 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0130 | PHYSICAL_SPAN | PZXL-00097-N0034 | PZXL-00097-N0035 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0131 | PHYSICAL_SPAN | PZXL-00097-N0072 | PZXL-00097-N0073 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0132 | PHYSICAL_SPAN | PZXL-00097-N0135 | PZXL-00097-N0136 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0133 | PHYSICAL_SPAN | PZXL-00097-N0006 | PZXL-00097-N0007 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0134 | PHYSICAL_SPAN | PZXL-00097-N0178 | PZXL-00097-N0179 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0135 | PHYSICAL_SPAN | PZXL-00097-N0035 | PZXL-00097-N0036 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0136 | PHYSICAL_SPAN | PZXL-00097-N0059 | PZXL-00097-N0060 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0137 | PHYSICAL_SPAN | PZXL-00097-N0068 | PZXL-00097-N0069 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0138 | PHYSICAL_SPAN | PZXL-00097-N0112 | PZXL-00097-N0113 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0139 | PHYSICAL_SPAN | PZXL-00097-N0102 | PZXL-00097-N0103 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0140 | PHYSICAL_SPAN | PZXL-00097-N0094 | PZXL-00097-N0095 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0141 | PHYSICAL_SPAN | PZXL-00097-N0101 | PZXL-00097-N0102 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0142 | PHYSICAL_SPAN | PZXL-00097-N0068 | PZXL-00097-N0098 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0143 | PHYSICAL_SPAN | PZXL-00097-N0091 | PZXL-00097-N0092 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0144 | PHYSICAL_SPAN | PZXL-00097-N0090 | PZXL-00097-N0091 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0145 | PHYSICAL_SPAN | PZXL-00097-N0098 | PZXL-00097-N0099 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0146 | PHYSICAL_SPAN | PZXL-00097-N0105 | PZXL-00097-N0106 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0147 | PHYSICAL_SPAN | PZXL-00097-N0092 | PZXL-00097-N0093 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0148 | PHYSICAL_SPAN | PZXL-00097-N0095 | PZXL-00097-N0096 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0149 | PHYSICAL_SPAN | PZXL-00097-N0099 | PZXL-00097-N0100 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0150 | PHYSICAL_SPAN | PZXL-00097-N0103 | PZXL-00097-N0104 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0151 | PHYSICAL_SPAN | PZXL-00097-N0104 | PZXL-00097-N0105 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0152 | PHYSICAL_SPAN | PZXL-00097-N0100 | PZXL-00097-N0101 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0153 | PHYSICAL_SPAN | PZXL-00097-N0106 | PZXL-00097-N0090 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0154 | PHYSICAL_SPAN | PZXL-00097-N0096 | PZXL-00097-N0097 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0155 | PHYSICAL_SPAN | PZXL-00097-N0093 | PZXL-00097-N0094 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0156 | PHYSICAL_SPAN | PZXL-00097-N0001 | PZXL-00097-N0002 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0157 | PHYSICAL_SPAN | PZXL-00097-N0144 | PZXL-00097-N0112 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0158 | PHYSICAL_SPAN | PZXL-00097-N0045 | PZXL-00097-N0046 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0159 | PHYSICAL_SPAN | PZXL-00097-N0011 | PZXL-00097-N0022 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0160 | PHYSICAL_SPAN | PZXL-00097-N0086 | PZXL-00097-N0087 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0161 | PHYSICAL_SPAN | PZXL-00097-N0041 | PZXL-00097-N0042 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0162 | PHYSICAL_SPAN | PZXL-00097-N0038 | PZXL-00097-N0039 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0163 | PHYSICAL_SPAN | PZXL-00097-N0048 | PZXL-00097-N0049 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0164 | PHYSICAL_SPAN | PZXL-00097-N0050 | PZXL-00097-N0051 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0165 | PHYSICAL_SPAN | PZXL-00097-N0065 | PZXL-00097-N0066 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0166 | PHYSICAL_SPAN | PZXL-00097-N0063 | PZXL-00097-N0064 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0167 | PHYSICAL_SPAN | PZXL-00097-N0087 | PZXL-00097-N0089 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0168 | PHYSICAL_SPAN | PZXL-00097-N0040 | PZXL-00097-N0041 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0169 | PHYSICAL_SPAN | PZXL-00097-N0047 | PZXL-00097-N0048 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0170 | PHYSICAL_SPAN | PZXL-00097-N0066 | PZXL-00097-N0067 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0171 | PHYSICAL_SPAN | PZXL-00097-N0022 | PZXL-00097-N0033 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0172 | PHYSICAL_SPAN | PZXL-00097-N0062 | PZXL-00097-N0063 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0173 | PHYSICAL_SPAN | PZXL-00097-N0061 | PZXL-00097-N0062 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0174 | PHYSICAL_SPAN | PZXL-00097-N0057 | PZXL-00097-N0056 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0175 | PHYSICAL_SPAN | PZXL-00097-N0031 | PZXL-00097-N0111 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0176 | PHYSICAL_SPAN | PZXL-00097-N0118 | PZXL-00097-N0119 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0177 | PHYSICAL_SPAN | PZXL-00097-N0117 | PZXL-00097-N0118 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0178 | PHYSICAL_SPAN | PZXL-00097-N0121 | PZXL-00097-N0122 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0179 | PHYSICAL_SPAN | PZXL-00097-N0120 | PZXL-00097-N0121 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0180 | PHYSICAL_SPAN | PZXL-00097-N0122 | PZXL-00097-N0123 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0181 | PHYSICAL_SPAN | PZXL-00097-N0119 | PZXL-00097-N0120 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0182 | PHYSICAL_SPAN | PZXL-00097-N0123 | PZXL-00097-N0114 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0183 | PHYSICAL_SPAN | PZXL-00097-N0116 | PZXL-00097-N0117 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0184 | PHYSICAL_SPAN | PZXL-00097-N0115 | PZXL-00097-N0116 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0185 | PHYSICAL_SPAN | PZXL-00097-N0144 | PZXL-00097-N0115 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0186 | PHYSICAL_SPAN | PZXL-00097-N0127 | PZXL-00097-N0128 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0187 | PHYSICAL_SPAN | PZXL-00097-N0089 | PZXL-00097-N0124 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0188 | PHYSICAL_SPAN | PZXL-00097-N0126 | PZXL-00097-N0127 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0189 | PHYSICAL_SPAN | PZXL-00097-N0125 | PZXL-00097-N0126 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0190 | PHYSICAL_SPAN | PZXL-00097-N0128 | PZXL-00097-N0129 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00097-B0191 | PHYSICAL_SPAN | PZXL-00097-N0124 | PZXL-00097-N0125 | PZXL-00097 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV墩西线明细.xlsx
PZXL-00154-B0001 | PHYSICAL_SPAN | PZXL-00154-N0042 | PZXL-00154-N0168 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0002 | PHYSICAL_SPAN | PZXL-00154-N0055 | PZXL-00154-N0054 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0003 | PHYSICAL_SPAN | PZXL-00154-N0061 | PZXL-00154-N0062 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0004 | PHYSICAL_SPAN | PZXL-00154-N0086 | PZXL-00154-N0087 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0005 | PHYSICAL_SPAN | PZXL-00154-N0195 | PZXL-00154-N0196 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0006 | PHYSICAL_SPAN | PZXL-00154-N0010 | PZXL-00154-N0011 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0007 | PHYSICAL_SPAN | PZXL-00154-N0013 | PZXL-00154-N0014 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0008 | PHYSICAL_SPAN | PZXL-00154-N0178 | PZXL-00154-N0179 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0009 | PHYSICAL_SPAN | PZXL-00154-N0201 | PZXL-00154-N0202 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0010 | PHYSICAL_SPAN | PZXL-00154-N0019 | PZXL-00154-N0020 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0011 | PHYSICAL_SPAN | PZXL-00154-N0087 | PZXL-00154-N0088 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0012 | PHYSICAL_SPAN | PZXL-00154-N0196 | PZXL-00154-N0197 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0013 | PHYSICAL_SPAN | PZXL-00154-N0163 | PZXL-00154-N0164 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0014 | PHYSICAL_SPAN | PZXL-00154-N0011 | PZXL-00154-N0012 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0015 | PHYSICAL_SPAN | PZXL-00154-N0018 | PZXL-00154-N0019 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0016 | PHYSICAL_SPAN | PZXL-00154-N0181 | PZXL-00154-N0182 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0017 | PHYSICAL_SPAN | PZXL-00154-N0012 | PZXL-00154-N0013 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0018 | PHYSICAL_SPAN | PZXL-00154-N0091 | PZXL-00154-N0085 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0019 | PHYSICAL_SPAN | PZXL-00154-N0014 | PZXL-00154-N0015 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0020 | PHYSICAL_SPAN | PZXL-00154-N0166 | PZXL-00154-N0167 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0021 | PHYSICAL_SPAN | PZXL-00154-N0194 | PZXL-00154-N0195 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0022 | PHYSICAL_SPAN | PZXL-00154-N0005 | PZXL-00154-N0006 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0023 | PHYSICAL_SPAN | PZXL-00154-N0035 | PZXL-00154-N0036 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0024 | PHYSICAL_SPAN | PZXL-00154-N0065 | PZXL-00154-N0162 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0025 | PHYSICAL_SPAN | PZXL-00154-N0039 | PZXL-00154-N0040 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0026 | PHYSICAL_SPAN | PZXL-00154-N0069 | PZXL-00154-N0002 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0027 | PHYSICAL_SPAN | PZXL-00154-N0065 | PZXL-00154-N0152 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0028 | PHYSICAL_SPAN | PZXL-00154-N0041 | PZXL-00154-N0042 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0029 | PHYSICAL_SPAN | PZXL-00154-N0023 | PZXL-00154-N0024 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0030 | PHYSICAL_SPAN | PZXL-00154-N0024 | PZXL-00154-N0025 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0031 | PHYSICAL_SPAN | PZXL-00154-N0179 | PZXL-00154-N0180 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0032 | PHYSICAL_SPAN | PZXL-00154-N0177 | PZXL-00154-N0178 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0033 | PHYSICAL_SPAN | PZXL-00154-N0176 | PZXL-00154-N0177 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0034 | PHYSICAL_SPAN | PZXL-00154-N0015 | PZXL-00154-N0017 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0035 | PHYSICAL_SPAN | PZXL-00154-N0009 | PZXL-00154-N0010 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0036 | PHYSICAL_SPAN | PZXL-00154-N0165 | PZXL-00154-N0166 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0037 | PHYSICAL_SPAN | PZXL-00154-N0021 | PZXL-00154-N0194 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0038 | PHYSICAL_SPAN | PZXL-00154-N0114 | PZXL-00154-N0113 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0039 | PHYSICAL_SPAN | PZXL-00154-N0162 | PZXL-00154-N0163 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0040 | PHYSICAL_SPAN | PZXL-00154-N0153 | PZXL-00154-N0154 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0041 | PHYSICAL_SPAN | PZXL-00154-N0085 | PZXL-00154-N0086 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0042 | PHYSICAL_SPAN | PZXL-00154-N0085 | PZXL-00154-N0201 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0043 | PHYSICAL_SPAN | PZXL-00154-N0078 | PZXL-00154-N0079 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0044 | PHYSICAL_SPAN | PZXL-00154-N0087 | PZXL-00154-N0200 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0045 | PHYSICAL_SPAN | PZXL-00154-N0123 | PZXL-00154-N0124 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0046 | PHYSICAL_SPAN | PZXL-00154-N0026 | PZXL-00154-N0028 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0047 | PHYSICAL_SPAN | PZXL-00154-N0122 | PZXL-00154-N0123 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0048 | PHYSICAL_SPAN | PZXL-00154-N0134 | PZXL-00154-N0135 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0049 | PHYSICAL_SPAN | PZXL-00154-N0016 | PZXL-00154-N0027 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JLB3-35 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0050 | PHYSICAL_SPAN | PZXL-00154-N0038 | PZXL-00154-N0047 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0051 | PHYSICAL_SPAN | PZXL-00154-N0047 | PZXL-00154-N0059 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0052 | PHYSICAL_SPAN | PZXL-00154-N0030 | PZXL-00154-N0031 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0053 | PHYSICAL_SPAN | PZXL-00154-N0029 | PZXL-00154-N0030 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0054 | PHYSICAL_SPAN | PZXL-00154-N0028 | PZXL-00154-N0029 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0055 | PHYSICAL_SPAN | PZXL-00154-N0116 | PZXL-00154-N0117 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0056 | PHYSICAL_SPAN | PZXL-00154-N0108 | PZXL-00154-N0109 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0057 | PHYSICAL_SPAN | PZXL-00154-N0059 | PZXL-00154-N0070 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0058 | PHYSICAL_SPAN | PZXL-00154-N0090 | PZXL-00154-N0101 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0059 | PHYSICAL_SPAN | PZXL-00154-N0027 | PZXL-00154-N0038 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0060 | PHYSICAL_SPAN | PZXL-00154-N0125 | PZXL-00154-N0126 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0061 | PHYSICAL_SPAN | PZXL-00154-N0129 | PZXL-00154-N0130 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0062 | PHYSICAL_SPAN | PZXL-00154-N0111 | PZXL-00154-N0112 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0063 | PHYSICAL_SPAN | PZXL-00154-N0117 | PZXL-00154-N0118 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0064 | PHYSICAL_SPAN | PZXL-00154-N0070 | PZXL-00154-N0090 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0065 | PHYSICAL_SPAN | PZXL-00154-N0121 | PZXL-00154-N0122 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0066 | PHYSICAL_SPAN | PZXL-00154-N0020 | PZXL-00154-N0127 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0067 | PHYSICAL_SPAN | PZXL-00154-N0025 | PZXL-00154-N0026 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0068 | PHYSICAL_SPAN | PZXL-00154-N0110 | PZXL-00154-N0111 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0069 | PHYSICAL_SPAN | PZXL-00154-N0115 | PZXL-00154-N0116 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0070 | PHYSICAL_SPAN | PZXL-00154-N0119 | PZXL-00154-N0120 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0071 | PHYSICAL_SPAN | PZXL-00154-N0128 | PZXL-00154-N0129 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0072 | PHYSICAL_SPAN | PZXL-00154-N0132 | PZXL-00154-N0133 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0073 | PHYSICAL_SPAN | PZXL-00154-N0136 | PZXL-00154-N0137 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0074 | PHYSICAL_SPAN | PZXL-00154-N0069 | PZXL-00154-N0071 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0075 | PHYSICAL_SPAN | PZXL-00154-N0071 | PZXL-00154-N0072 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0076 | PHYSICAL_SPAN | PZXL-00154-N0072 | PZXL-00154-N0073 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0077 | PHYSICAL_SPAN | PZXL-00154-N0065 | PZXL-00154-N0066 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0078 | PHYSICAL_SPAN | PZXL-00154-N0057 | PZXL-00154-N0058 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0079 | PHYSICAL_SPAN | PZXL-00154-N0056 | PZXL-00154-N0057 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0080 | PHYSICAL_SPAN | PZXL-00154-N0052 | PZXL-00154-N0053 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0081 | PHYSICAL_SPAN | PZXL-00154-N0053 | PZXL-00154-N0055 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0082 | PHYSICAL_SPAN | PZXL-00154-N0055 | PZXL-00154-N0056 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0083 | PHYSICAL_SPAN | PZXL-00154-N0051 | PZXL-00154-N0052 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0084 | PHYSICAL_SPAN | PZXL-00154-N0050 | PZXL-00154-N0051 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0085 | PHYSICAL_SPAN | PZXL-00154-N0062 | PZXL-00154-N0063 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0086 | PHYSICAL_SPAN | PZXL-00154-N0063 | PZXL-00154-N0064 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0087 | PHYSICAL_SPAN | PZXL-00154-N0064 | PZXL-00154-N0065 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0088 | PHYSICAL_SPAN | PZXL-00154-N0104 | PZXL-00154-N0105 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0089 | PHYSICAL_SPAN | PZXL-00154-N0092 | PZXL-00154-N0093 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0090 | PHYSICAL_SPAN | PZXL-00154-N0093 | PZXL-00154-N0094 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0091 | PHYSICAL_SPAN | PZXL-00154-N0094 | PZXL-00154-N0095 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0092 | PHYSICAL_SPAN | PZXL-00154-N0095 | PZXL-00154-N0096 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0093 | PHYSICAL_SPAN | PZXL-00154-N0096 | PZXL-00154-N0097 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0094 | PHYSICAL_SPAN | PZXL-00154-N0097 | PZXL-00154-N0098 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0095 | PHYSICAL_SPAN | PZXL-00154-N0084 | PZXL-00154-N0089 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0096 | PHYSICAL_SPAN | PZXL-00154-N0130 | PZXL-00154-N0131 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0097 | PHYSICAL_SPAN | PZXL-00154-N0118 | PZXL-00154-N0119 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0098 | PHYSICAL_SPAN | PZXL-00154-N0124 | PZXL-00154-N0125 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0099 | PHYSICAL_SPAN | PZXL-00154-N0133 | PZXL-00154-N0134 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0100 | PHYSICAL_SPAN | PZXL-00154-N0042 | PZXL-00154-N0043 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0101 | PHYSICAL_SPAN | PZXL-00154-N0109 | PZXL-00154-N0110 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0102 | PHYSICAL_SPAN | PZXL-00154-N0112 | PZXL-00154-N0114 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0103 | PHYSICAL_SPAN | PZXL-00154-N0022 | PZXL-00154-N0023 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0104 | PHYSICAL_SPAN | PZXL-00154-N0120 | PZXL-00154-N0121 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0105 | PHYSICAL_SPAN | PZXL-00154-N0101 | PZXL-00154-N0106 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0106 | PHYSICAL_SPAN | PZXL-00154-N0131 | PZXL-00154-N0132 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JL(GD)/GIA-240/40 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0107 | PHYSICAL_SPAN | PZXL-00154-N0059 | PZXL-00154-N0165 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0108 | PHYSICAL_SPAN | PZXL-00154-N0077 | PZXL-00154-N0078 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0109 | PHYSICAL_SPAN | PZXL-00154-N0008 | PZXL-00154-N0009 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0110 | PHYSICAL_SPAN | PZXL-00154-N0037 | PZXL-00154-N0039 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0111 | PHYSICAL_SPAN | PZXL-00154-N0073 | PZXL-00154-N0074 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0112 | PHYSICAL_SPAN | PZXL-00154-N0048 | PZXL-00154-N0049 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0113 | PHYSICAL_SPAN | PZXL-00154-N0049 | PZXL-00154-N0050 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0114 | PHYSICAL_SPAN | PZXL-00154-N0060 | PZXL-00154-N0061 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0115 | PHYSICAL_SPAN | PZXL-00154-N0046 | PZXL-00154-N0048 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0116 | PHYSICAL_SPAN | PZXL-00154-N0193 | PZXL-00154-N0046 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0117 | PHYSICAL_SPAN | PZXL-00154-N0045 | PZXL-00154-N0193 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0118 | PHYSICAL_SPAN | PZXL-00154-N0058 | PZXL-00154-N0060 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0119 | PHYSICAL_SPAN | PZXL-00154-N0148 | PZXL-00154-N0149 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0120 | PHYSICAL_SPAN | PZXL-00154-N0147 | PZXL-00154-N0148 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0121 | PHYSICAL_SPAN | PZXL-00154-N0145 | PZXL-00154-N0146 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0122 | PHYSICAL_SPAN | PZXL-00154-N0146 | PZXL-00154-N0147 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0123 | PHYSICAL_SPAN | PZXL-00154-N0080 | PZXL-00154-N0138 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0124 | PHYSICAL_SPAN | PZXL-00154-N0138 | PZXL-00154-N0139 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0125 | PHYSICAL_SPAN | PZXL-00154-N0139 | PZXL-00154-N0140 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0126 | PHYSICAL_SPAN | PZXL-00154-N0140 | PZXL-00154-N0141 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0127 | PHYSICAL_SPAN | PZXL-00154-N0141 | PZXL-00154-N0142 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0128 | PHYSICAL_SPAN | PZXL-00154-N0089 | PZXL-00154-N0091 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0129 | PHYSICAL_SPAN | PZXL-00154-N0091 | PZXL-00154-N0092 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0130 | PHYSICAL_SPAN | PZXL-00154-N0080 | PZXL-00154-N0081 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0131 | PHYSICAL_SPAN | PZXL-00154-N0192 | PZXL-00154-N0041 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0132 | PHYSICAL_SPAN | PZXL-00154-N0081 | PZXL-00154-N0082 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0133 | PHYSICAL_SPAN | PZXL-00154-N0082 | PZXL-00154-N0083 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0134 | PHYSICAL_SPAN | PZXL-00154-N0083 | PZXL-00154-N0084 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0135 | PHYSICAL_SPAN | PZXL-00154-N0182 | PZXL-00154-N0183 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0136 | PHYSICAL_SPAN | PZXL-00154-N0183 | PZXL-00154-N0184 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0137 | PHYSICAL_SPAN | PZXL-00154-N0184 | PZXL-00154-N0185 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0138 | PHYSICAL_SPAN | PZXL-00154-N0185 | PZXL-00154-N0186 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0139 | PHYSICAL_SPAN | PZXL-00154-N0186 | PZXL-00154-N0187 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0140 | PHYSICAL_SPAN | PZXL-00154-N0187 | PZXL-00154-N0188 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0141 | PHYSICAL_SPAN | PZXL-00154-N0188 | PZXL-00154-N0189 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0142 | PHYSICAL_SPAN | PZXL-00154-N0189 | PZXL-00154-N0190 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0143 | PHYSICAL_SPAN | PZXL-00154-N0075 | PZXL-00154-N0076 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0144 | PHYSICAL_SPAN | PZXL-00154-N0044 | PZXL-00154-N0045 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0145 | PHYSICAL_SPAN | PZXL-00154-N0021 | PZXL-00154-N0022 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0146 | PHYSICAL_SPAN | PZXL-00154-N0114 | PZXL-00154-N0115 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0147 | PHYSICAL_SPAN | PZXL-00154-N0017 | PZXL-00154-N0018 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0148 | PHYSICAL_SPAN | PZXL-00154-N0031 | PZXL-00154-N0032 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0149 | PHYSICAL_SPAN | PZXL-00154-N0036 | PZXL-00154-N0037 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0150 | PHYSICAL_SPAN | PZXL-00154-N0033 | PZXL-00154-N0034 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0151 | PHYSICAL_SPAN | PZXL-00154-N0034 | PZXL-00154-N0035 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0152 | PHYSICAL_SPAN | PZXL-00154-N0032 | PZXL-00154-N0033 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0153 | PHYSICAL_SPAN | PZXL-00154-N0066 | PZXL-00154-N0067 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0154 | PHYSICAL_SPAN | PZXL-00154-N0067 | PZXL-00154-N0068 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0155 | PHYSICAL_SPAN | PZXL-00154-N0068 | PZXL-00154-N0069 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0156 | PHYSICAL_SPAN | PZXL-00154-N0142 | PZXL-00154-N0143 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0157 | PHYSICAL_SPAN | PZXL-00154-N0143 | PZXL-00154-N0144 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0158 | PHYSICAL_SPAN | PZXL-00154-N0144 | PZXL-00154-N0145 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0159 | PHYSICAL_SPAN | PZXL-00154-N0192 | PZXL-00154-N0107 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0160 | PHYSICAL_SPAN | PZXL-00154-N0107 | PZXL-00154-N0108 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0161 | PHYSICAL_SPAN | PZXL-00154-N0043 | PZXL-00154-N0044 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0162 | PHYSICAL_SPAN | PZXL-00154-N0169 | PZXL-00154-N0170 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0163 | PHYSICAL_SPAN | PZXL-00154-N0170 | PZXL-00154-N0171 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0164 | PHYSICAL_SPAN | PZXL-00154-N0171 | PZXL-00154-N0172 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0165 | PHYSICAL_SPAN | PZXL-00154-N0076 | PZXL-00154-N0077 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0166 | PHYSICAL_SPAN | PZXL-00154-N0141 | PZXL-00154-N0155 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0167 | PHYSICAL_SPAN | PZXL-00154-N0152 | PZXL-00154-N0153 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0168 | PHYSICAL_SPAN | PZXL-00154-N0080 | PZXL-00154-N0075 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0169 | PHYSICAL_SPAN | PZXL-00154-N0100 | PZXL-00154-N0102 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0170 | PHYSICAL_SPAN | PZXL-00154-N0172 | PZXL-00154-N0173 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0171 | PHYSICAL_SPAN | PZXL-00154-N0173 | PZXL-00154-N0174 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0172 | PHYSICAL_SPAN | PZXL-00154-N0174 | PZXL-00154-N0175 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0173 | PHYSICAL_SPAN | PZXL-00154-N0175 | PZXL-00154-N0176 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0174 | PHYSICAL_SPAN | PZXL-00154-N0149 | PZXL-00154-N0150 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0175 | PHYSICAL_SPAN | PZXL-00154-N0150 | PZXL-00154-N0151 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0176 | PHYSICAL_SPAN | PZXL-00154-N0002 | PZXL-00154-N0003 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0177 | PHYSICAL_SPAN | PZXL-00154-N0003 | PZXL-00154-N0004 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0178 | PHYSICAL_SPAN | PZXL-00154-N0002 | PZXL-00154-N0001 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0179 | PHYSICAL_SPAN | PZXL-00154-N0045 | PZXL-00154-N0191 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0180 | PHYSICAL_SPAN | PZXL-00154-N0168 | PZXL-00154-N0169 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0181 | PHYSICAL_SPAN | PZXL-00154-N0102 | PZXL-00154-N0103 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0182 | PHYSICAL_SPAN | PZXL-00154-N0103 | PZXL-00154-N0104 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0183 | PHYSICAL_SPAN | PZXL-00154-N0099 | PZXL-00154-N0100 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0184 | PHYSICAL_SPAN | PZXL-00154-N0098 | PZXL-00154-N0099 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0185 | PHYSICAL_SPAN | PZXL-00154-N0180 | PZXL-00154-N0181 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0186 | PHYSICAL_SPAN | PZXL-00154-N0156 | PZXL-00154-N0157 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0187 | PHYSICAL_SPAN | PZXL-00154-N0159 | PZXL-00154-N0160 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0188 | PHYSICAL_SPAN | PZXL-00154-N0112 | PZXL-00154-N0156 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0189 | PHYSICAL_SPAN | PZXL-00154-N0198 | PZXL-00154-N0199 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0190 | PHYSICAL_SPAN | PZXL-00154-N0036 | PZXL-00154-N0159 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0191 | PHYSICAL_SPAN | PZXL-00154-N0197 | PZXL-00154-N0198 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0192 | PHYSICAL_SPAN | PZXL-00154-N0160 | PZXL-00154-N0161 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0193 | PHYSICAL_SPAN | PZXL-00154-N0157 | PZXL-00154-N0158 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0194 | PHYSICAL_SPAN | PZXL-00154-N0007 | PZXL-00154-N0008 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00154-B0195 | PHYSICAL_SPAN | PZXL-00154-N0135 | PZXL-00154-N0136 | PZXL-00154 | CLOSED | CLOSED | YES | 50 | JKLGYJ-240 | R_X_IMAX_PENDING | 邳州_10kV河东线明细.xlsx
PZXL-00161-B0001 | PHYSICAL_SPAN | PZXL-00161-N0074 | PZXL-00161-N0075 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ/QN-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0002 | PHYSICAL_SPAN | PZXL-00161-N0065 | PZXL-00161-N0066 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0003 | PHYSICAL_SPAN | PZXL-00161-N0032 | PZXL-00161-N0033 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0004 | PHYSICAL_SPAN | PZXL-00161-N0002 | PZXL-00161-N0003 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0005 | PHYSICAL_SPAN | PZXL-00161-N0006 | PZXL-00161-N0007 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0006 | PHYSICAL_SPAN | PZXL-00161-N0016 | PZXL-00161-N0017 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0007 | PHYSICAL_SPAN | PZXL-00161-N0018 | PZXL-00161-N0019 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0008 | PHYSICAL_SPAN | PZXL-00161-N0029 | PZXL-00161-N0030 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0009 | PHYSICAL_SPAN | PZXL-00161-N0005 | PZXL-00161-N0006 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0010 | PHYSICAL_SPAN | PZXL-00161-N0008 | PZXL-00161-N0009 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0011 | PHYSICAL_SPAN | PZXL-00161-N0028 | PZXL-00161-N0029 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0012 | PHYSICAL_SPAN | PZXL-00161-N0023 | PZXL-00161-N0024 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0013 | PHYSICAL_SPAN | PZXL-00161-N0030 | PZXL-00161-N0031 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0014 | PHYSICAL_SPAN | PZXL-00161-N0061 | PZXL-00161-N0062 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0015 | PHYSICAL_SPAN | PZXL-00161-N0034 | PZXL-00161-N0035 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0016 | PHYSICAL_SPAN | PZXL-00161-N0040 | PZXL-00161-N0041 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0017 | PHYSICAL_SPAN | PZXL-00161-N0003 | PZXL-00161-N0004 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0018 | PHYSICAL_SPAN | PZXL-00161-N0062 | PZXL-00161-N0063 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0019 | PHYSICAL_SPAN | PZXL-00161-N0019 | PZXL-00161-N0020 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0020 | PHYSICAL_SPAN | PZXL-00161-N0033 | PZXL-00161-N0034 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0021 | PHYSICAL_SPAN | PZXL-00161-N0038 | PZXL-00161-N0039 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0022 | PHYSICAL_SPAN | PZXL-00161-N0058 | PZXL-00161-N0059 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0023 | PHYSICAL_SPAN | PZXL-00161-N0057 | PZXL-00161-N0058 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0024 | PHYSICAL_SPAN | PZXL-00161-N0051 | PZXL-00161-N0052 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0025 | PHYSICAL_SPAN | PZXL-00161-N0050 | PZXL-00161-N0051 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0026 | PHYSICAL_SPAN | PZXL-00161-N0052 | PZXL-00161-N0053 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0027 | PHYSICAL_SPAN | PZXL-00161-N0056 | PZXL-00161-N0057 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0028 | PHYSICAL_SPAN | PZXL-00161-N0049 | PZXL-00161-N0050 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0029 | PHYSICAL_SPAN | PZXL-00161-N0055 | PZXL-00161-N0056 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0030 | PHYSICAL_SPAN | PZXL-00161-N0053 | PZXL-00161-N0054 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0031 | PHYSICAL_SPAN | PZXL-00161-N0060 | PZXL-00161-N0061 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0032 | PHYSICAL_SPAN | PZXL-00161-N0009 | PZXL-00161-N0010 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0033 | PHYSICAL_SPAN | PZXL-00161-N0035 | PZXL-00161-N0036 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0034 | PHYSICAL_SPAN | PZXL-00161-N0037 | PZXL-00161-N0038 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0035 | PHYSICAL_SPAN | PZXL-00161-N0014 | PZXL-00161-N0015 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0036 | PHYSICAL_SPAN | PZXL-00161-N0013 | PZXL-00161-N0014 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0037 | PHYSICAL_SPAN | PZXL-00161-N0048 | PZXL-00161-N0049 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0038 | PHYSICAL_SPAN | PZXL-00161-N0047 | PZXL-00161-N0048 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0039 | PHYSICAL_SPAN | PZXL-00161-N0044 | PZXL-00161-N0045 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0040 | PHYSICAL_SPAN | PZXL-00161-N0046 | PZXL-00161-N0047 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0041 | PHYSICAL_SPAN | PZXL-00161-N0045 | PZXL-00161-N0046 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0042 | PHYSICAL_SPAN | PZXL-00161-N0054 | PZXL-00161-N0055 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0043 | PHYSICAL_SPAN | PZXL-00161-N0015 | PZXL-00161-N0016 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0044 | PHYSICAL_SPAN | PZXL-00161-N0021 | PZXL-00161-N0022 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0045 | PHYSICAL_SPAN | PZXL-00161-N0022 | PZXL-00161-N0023 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0046 | PHYSICAL_SPAN | PZXL-00161-N0031 | PZXL-00161-N0032 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0047 | PHYSICAL_SPAN | PZXL-00161-N0011 | PZXL-00161-N0012 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0048 | PHYSICAL_SPAN | PZXL-00161-N0027 | PZXL-00161-N0028 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0049 | PHYSICAL_SPAN | PZXL-00161-N0007 | PZXL-00161-N0008 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0050 | PHYSICAL_SPAN | PZXL-00161-N0026 | PZXL-00161-N0027 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0051 | PHYSICAL_SPAN | PZXL-00161-N0004 | PZXL-00161-N0005 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0052 | PHYSICAL_SPAN | PZXL-00161-N0064 | PZXL-00161-N0065 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0053 | PHYSICAL_SPAN | PZXL-00161-N0024 | PZXL-00161-N0025 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0054 | PHYSICAL_SPAN | PZXL-00161-N0039 | PZXL-00161-N0040 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0055 | PHYSICAL_SPAN | PZXL-00161-N0001 | PZXL-00161-N0002 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0056 | PHYSICAL_SPAN | PZXL-00161-N0020 | PZXL-00161-N0021 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0057 | PHYSICAL_SPAN | PZXL-00161-N0041 | PZXL-00161-N0042 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0058 | PHYSICAL_SPAN | PZXL-00161-N0017 | PZXL-00161-N0018 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0059 | PHYSICAL_SPAN | PZXL-00161-N0025 | PZXL-00161-N0026 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0060 | PHYSICAL_SPAN | PZXL-00161-N0010 | PZXL-00161-N0011 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0061 | PHYSICAL_SPAN | PZXL-00161-N0012 | PZXL-00161-N0013 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | LGJ-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0062 | PHYSICAL_SPAN | PZXL-00161-N0063 | PZXL-00161-N0064 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ-150 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0063 | PHYSICAL_SPAN | PZXL-00161-N0077 | PZXL-00161-N0078 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ/QN-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0064 | PHYSICAL_SPAN | PZXL-00161-N0052 | PZXL-00161-N0074 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ/QN-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0065 | PHYSICAL_SPAN | PZXL-00161-N0075 | PZXL-00161-N0076 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ/QN-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0066 | PHYSICAL_SPAN | PZXL-00161-N0076 | PZXL-00161-N0077 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JKLYJ/QN-10-240 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0067 | PHYSICAL_SPAN | PZXL-00161-N0072 | PZXL-00161-N0073 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0068 | PHYSICAL_SPAN | PZXL-00161-N0067 | PZXL-00161-N0068 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0069 | PHYSICAL_SPAN | PZXL-00161-N0070 | PZXL-00161-N0067 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0070 | PHYSICAL_SPAN | PZXL-00161-N0043 | PZXL-00161-N0071 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0071 | PHYSICAL_SPAN | PZXL-00161-N0069 | PZXL-00161-N0070 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00161-B0072 | PHYSICAL_SPAN | PZXL-00161-N0066 | PZXL-00161-N0069 | PZXL-00161 | CLOSED | CLOSED | YES | 50 | JL/G1A-240/30 | R_X_IMAX_PENDING | 邳州_10kV河炮线明细.xlsx
PZXL-00173-B0001 | PHYSICAL_SPAN | PZXL-00173-N0054 | PZXL-00173-N0099 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0002 | PHYSICAL_SPAN | PZXL-00173-N0190 | PZXL-00173-N0191 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0003 | PHYSICAL_SPAN | PZXL-00173-N0192 | PZXL-00173-N0193 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0004 | PHYSICAL_SPAN | PZXL-00173-N0189 | PZXL-00173-N0190 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0005 | PHYSICAL_SPAN | PZXL-00173-N0193 | PZXL-00173-N0194 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0006 | PHYSICAL_SPAN | PZXL-00173-N0191 | PZXL-00173-N0192 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0007 | PHYSICAL_SPAN | PZXL-00173-N0194 | PZXL-00173-N0195 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0008 | PHYSICAL_SPAN | PZXL-00173-N0001 | PZXL-00173-N0002 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0009 | PHYSICAL_SPAN | PZXL-00173-N0059 | PZXL-00173-N0060 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0010 | PHYSICAL_SPAN | PZXL-00173-N0126 | PZXL-00173-N0127 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0011 | PHYSICAL_SPAN | PZXL-00173-N0111 | PZXL-00173-N0112 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0012 | PHYSICAL_SPAN | PZXL-00173-N0117 | PZXL-00173-N0118 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0013 | PHYSICAL_SPAN | PZXL-00173-N0122 | PZXL-00173-N0123 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0014 | PHYSICAL_SPAN | PZXL-00173-N0114 | PZXL-00173-N0115 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0015 | PHYSICAL_SPAN | PZXL-00173-N0115 | PZXL-00173-N0116 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0016 | PHYSICAL_SPAN | PZXL-00173-N0110 | PZXL-00173-N0111 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0017 | PHYSICAL_SPAN | PZXL-00173-N0127 | PZXL-00173-N0109 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0018 | PHYSICAL_SPAN | PZXL-00173-N0125 | PZXL-00173-N0126 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0019 | PHYSICAL_SPAN | PZXL-00173-N0120 | PZXL-00173-N0121 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0020 | PHYSICAL_SPAN | PZXL-00173-N0123 | PZXL-00173-N0124 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0021 | PHYSICAL_SPAN | PZXL-00173-N0096 | PZXL-00173-N0119 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0022 | PHYSICAL_SPAN | PZXL-00173-N0116 | PZXL-00173-N0117 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0023 | PHYSICAL_SPAN | PZXL-00173-N0124 | PZXL-00173-N0125 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0024 | PHYSICAL_SPAN | PZXL-00173-N0121 | PZXL-00173-N0122 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0025 | PHYSICAL_SPAN | PZXL-00173-N0113 | PZXL-00173-N0114 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0026 | PHYSICAL_SPAN | PZXL-00173-N0112 | PZXL-00173-N0113 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0027 | PHYSICAL_SPAN | PZXL-00173-N0109 | PZXL-00173-N0110 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0028 | PHYSICAL_SPAN | PZXL-00173-N0119 | PZXL-00173-N0120 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0029 | PHYSICAL_SPAN | PZXL-00173-N0213 | PZXL-00173-N0214 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0030 | PHYSICAL_SPAN | PZXL-00173-N0208 | PZXL-00173-N0209 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0031 | PHYSICAL_SPAN | PZXL-00173-N0211 | PZXL-00173-N0212 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0032 | PHYSICAL_SPAN | PZXL-00173-N0224 | PZXL-00173-N0225 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0033 | PHYSICAL_SPAN | PZXL-00173-N0206 | PZXL-00173-N0217 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0034 | PHYSICAL_SPAN | PZXL-00173-N0221 | PZXL-00173-N0222 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0035 | PHYSICAL_SPAN | PZXL-00173-N0197 | PZXL-00173-N0198 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0036 | PHYSICAL_SPAN | PZXL-00173-N0196 | PZXL-00173-N0197 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0037 | PHYSICAL_SPAN | PZXL-00173-N0210 | PZXL-00173-N0211 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0038 | PHYSICAL_SPAN | PZXL-00173-N0222 | PZXL-00173-N0223 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0039 | PHYSICAL_SPAN | PZXL-00173-N0223 | PZXL-00173-N0224 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0040 | PHYSICAL_SPAN | PZXL-00173-N0204 | PZXL-00173-N0205 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0041 | PHYSICAL_SPAN | PZXL-00173-N0217 | PZXL-00173-N0219 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0042 | PHYSICAL_SPAN | PZXL-00173-N0207 | PZXL-00173-N0208 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0043 | PHYSICAL_SPAN | PZXL-00173-N0220 | PZXL-00173-N0221 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0044 | PHYSICAL_SPAN | PZXL-00173-N0202 | PZXL-00173-N0203 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0045 | PHYSICAL_SPAN | PZXL-00173-N0199 | PZXL-00173-N0200 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0046 | PHYSICAL_SPAN | PZXL-00173-N0225 | PZXL-00173-N0196 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0047 | PHYSICAL_SPAN | PZXL-00173-N0200 | PZXL-00173-N0201 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0048 | PHYSICAL_SPAN | PZXL-00173-N0209 | PZXL-00173-N0210 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0049 | PHYSICAL_SPAN | PZXL-00173-N0219 | PZXL-00173-N0220 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0050 | PHYSICAL_SPAN | PZXL-00173-N0047 | PZXL-00173-N0206 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0051 | PHYSICAL_SPAN | PZXL-00173-N0216 | PZXL-00173-N0218 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0052 | PHYSICAL_SPAN | PZXL-00173-N0205 | PZXL-00173-N0207 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0053 | PHYSICAL_SPAN | PZXL-00173-N0203 | PZXL-00173-N0204 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0054 | PHYSICAL_SPAN | PZXL-00173-N0214 | PZXL-00173-N0215 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0055 | PHYSICAL_SPAN | PZXL-00173-N0212 | PZXL-00173-N0213 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0056 | PHYSICAL_SPAN | PZXL-00173-N0215 | PZXL-00173-N0216 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0057 | PHYSICAL_SPAN | PZXL-00173-N0198 | PZXL-00173-N0199 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0058 | PHYSICAL_SPAN | PZXL-00173-N0201 | PZXL-00173-N0202 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0059 | PHYSICAL_SPAN | PZXL-00173-N0039 | PZXL-00173-N0132 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0060 | PHYSICAL_SPAN | PZXL-00173-N0036 | PZXL-00173-N0037 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0061 | PHYSICAL_SPAN | PZXL-00173-N0143 | PZXL-00173-N0144 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0062 | PHYSICAL_SPAN | PZXL-00173-N0005 | PZXL-00173-N0006 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0063 | PHYSICAL_SPAN | PZXL-00173-N0146 | PZXL-00173-N0147 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0064 | PHYSICAL_SPAN | PZXL-00173-N0132 | PZXL-00173-N0133 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0065 | PHYSICAL_SPAN | PZXL-00173-N0046 | PZXL-00173-N0047 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0066 | PHYSICAL_SPAN | PZXL-00173-N0012 | PZXL-00173-N0013 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0067 | PHYSICAL_SPAN | PZXL-00173-N0135 | PZXL-00173-N0136 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0068 | PHYSICAL_SPAN | PZXL-00173-N0010 | PZXL-00173-N0011 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0069 | PHYSICAL_SPAN | PZXL-00173-N0011 | PZXL-00173-N0012 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0070 | PHYSICAL_SPAN | PZXL-00173-N0154 | PZXL-00173-N0155 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0071 | PHYSICAL_SPAN | PZXL-00173-N0155 | PZXL-00173-N0156 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0072 | PHYSICAL_SPAN | PZXL-00173-N0156 | PZXL-00173-N0157 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0073 | PHYSICAL_SPAN | PZXL-00173-N0187 | PZXL-00173-N0188 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0074 | PHYSICAL_SPAN | PZXL-00173-N0186 | PZXL-00173-N0187 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0075 | PHYSICAL_SPAN | PZXL-00173-N0188 | PZXL-00173-N0189 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0076 | PHYSICAL_SPAN | PZXL-00173-N0072 | PZXL-00173-N0078 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0077 | PHYSICAL_SPAN | PZXL-00173-N0078 | PZXL-00173-N0079 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0078 | PHYSICAL_SPAN | PZXL-00173-N0138 | PZXL-00173-N0139 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0079 | PHYSICAL_SPAN | PZXL-00173-N0185 | PZXL-00173-N0186 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0080 | PHYSICAL_SPAN | PZXL-00173-N0171 | PZXL-00173-N0240 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0081 | PHYSICAL_SPAN | PZXL-00173-N0180 | PZXL-00173-N0181 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0082 | PHYSICAL_SPAN | PZXL-00173-N0153 | PZXL-00173-N0154 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0083 | PHYSICAL_SPAN | PZXL-00173-N0171 | PZXL-00173-N0172 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0084 | PHYSICAL_SPAN | PZXL-00173-N0183 | PZXL-00173-N0184 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0085 | PHYSICAL_SPAN | PZXL-00173-N0152 | PZXL-00173-N0153 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0086 | PHYSICAL_SPAN | PZXL-00173-N0177 | PZXL-00173-N0150 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0087 | PHYSICAL_SPAN | PZXL-00173-N0173 | PZXL-00173-N0174 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0088 | PHYSICAL_SPAN | PZXL-00173-N0150 | PZXL-00173-N0151 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0089 | PHYSICAL_SPAN | PZXL-00173-N0176 | PZXL-00173-N0177 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0090 | PHYSICAL_SPAN | PZXL-00173-N0174 | PZXL-00173-N0175 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0091 | PHYSICAL_SPAN | PZXL-00173-N0175 | PZXL-00173-N0176 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0092 | PHYSICAL_SPAN | PZXL-00173-N0172 | PZXL-00173-N0173 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0093 | PHYSICAL_SPAN | PZXL-00173-N0177 | PZXL-00173-N0178 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0094 | PHYSICAL_SPAN | PZXL-00173-N0158 | PZXL-00173-N0159 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0095 | PHYSICAL_SPAN | PZXL-00173-N0160 | PZXL-00173-N0161 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0096 | PHYSICAL_SPAN | PZXL-00173-N0161 | PZXL-00173-N0162 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0097 | PHYSICAL_SPAN | PZXL-00173-N0162 | PZXL-00173-N0163 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0098 | PHYSICAL_SPAN | PZXL-00173-N0163 | PZXL-00173-N0164 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0099 | PHYSICAL_SPAN | PZXL-00173-N0165 | PZXL-00173-N0166 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0100 | PHYSICAL_SPAN | PZXL-00173-N0166 | PZXL-00173-N0167 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0101 | PHYSICAL_SPAN | PZXL-00173-N0151 | PZXL-00173-N0152 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0102 | PHYSICAL_SPAN | PZXL-00173-N0178 | PZXL-00173-N0179 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0103 | PHYSICAL_SPAN | PZXL-00173-N0179 | PZXL-00173-N0180 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0104 | PHYSICAL_SPAN | PZXL-00173-N0181 | PZXL-00173-N0182 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0105 | PHYSICAL_SPAN | PZXL-00173-N0182 | PZXL-00173-N0183 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0106 | PHYSICAL_SPAN | PZXL-00173-N0184 | PZXL-00173-N0185 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0107 | PHYSICAL_SPAN | PZXL-00173-N0167 | PZXL-00173-N0168 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0108 | PHYSICAL_SPAN | PZXL-00173-N0168 | PZXL-00173-N0169 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0109 | PHYSICAL_SPAN | PZXL-00173-N0169 | PZXL-00173-N0170 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0110 | PHYSICAL_SPAN | PZXL-00173-N0170 | PZXL-00173-N0171 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0111 | PHYSICAL_SPAN | PZXL-00173-N0164 | PZXL-00173-N0165 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0112 | PHYSICAL_SPAN | PZXL-00173-N0086 | PZXL-00173-N0158 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0113 | PHYSICAL_SPAN | PZXL-00173-N0159 | PZXL-00173-N0160 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0114 | PHYSICAL_SPAN | PZXL-00173-N0161 | PZXL-00173-N0229 | PZXL-00173 | CLOSED | CLOSED | YES | 50 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0115 | PHYSICAL_SPAN | PZXL-00173-N0020 | PZXL-00173-N0230 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0116 | PHYSICAL_SPAN | PZXL-00173-N0236 | PZXL-00173-N0237 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0117 | PHYSICAL_SPAN | PZXL-00173-N0042 | PZXL-00173-N0043 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0118 | PHYSICAL_SPAN | PZXL-00173-N0045 | PZXL-00173-N0046 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0119 | PHYSICAL_SPAN | PZXL-00173-N0235 | PZXL-00173-N0236 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0120 | PHYSICAL_SPAN | PZXL-00173-N0027 | PZXL-00173-N0028 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0121 | PHYSICAL_SPAN | PZXL-00173-N0147 | PZXL-00173-N0148 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0122 | PHYSICAL_SPAN | PZXL-00173-N0033 | PZXL-00173-N0034 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0123 | PHYSICAL_SPAN | PZXL-00173-N0044 | PZXL-00173-N0045 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0124 | PHYSICAL_SPAN | PZXL-00173-N0015 | PZXL-00173-N0016 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0125 | PHYSICAL_SPAN | PZXL-00173-N0026 | PZXL-00173-N0027 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0126 | PHYSICAL_SPAN | PZXL-00173-N0028 | PZXL-00173-N0029 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0127 | PHYSICAL_SPAN | PZXL-00173-N0098 | PZXL-00173-N0044 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0128 | PHYSICAL_SPAN | PZXL-00173-N0232 | PZXL-00173-N0233 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0129 | PHYSICAL_SPAN | PZXL-00173-N0041 | PZXL-00173-N0042 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0130 | PHYSICAL_SPAN | PZXL-00173-N0134 | PZXL-00173-N0226 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0131 | PHYSICAL_SPAN | PZXL-00173-N0017 | PZXL-00173-N0018 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0132 | PHYSICAL_SPAN | PZXL-00173-N0022 | PZXL-00173-N0023 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0133 | PHYSICAL_SPAN | PZXL-00173-N0020 | PZXL-00173-N0021 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0134 | PHYSICAL_SPAN | PZXL-00173-N0141 | PZXL-00173-N0142 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0135 | PHYSICAL_SPAN | PZXL-00173-N0019 | PZXL-00173-N0020 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0136 | PHYSICAL_SPAN | PZXL-00173-N0038 | PZXL-00173-N0039 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0137 | PHYSICAL_SPAN | PZXL-00173-N0234 | PZXL-00173-N0235 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0138 | PHYSICAL_SPAN | PZXL-00173-N0014 | PZXL-00173-N0015 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0139 | PHYSICAL_SPAN | PZXL-00173-N0016 | PZXL-00173-N0017 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0140 | PHYSICAL_SPAN | PZXL-00173-N0025 | PZXL-00173-N0026 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0141 | PHYSICAL_SPAN | PZXL-00173-N0133 | PZXL-00173-N0134 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0142 | PHYSICAL_SPAN | PZXL-00173-N0040 | PZXL-00173-N0041 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0143 | PHYSICAL_SPAN | PZXL-00173-N0134 | PZXL-00173-N0135 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0144 | PHYSICAL_SPAN | PZXL-00173-N0226 | PZXL-00173-N0227 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0145 | PHYSICAL_SPAN | PZXL-00173-N0013 | PZXL-00173-N0014 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0146 | PHYSICAL_SPAN | PZXL-00173-N0030 | PZXL-00173-N0031 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0147 | PHYSICAL_SPAN | PZXL-00173-N0024 | PZXL-00173-N0025 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0148 | PHYSICAL_SPAN | PZXL-00173-N0003 | PZXL-00173-N0004 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0149 | PHYSICAL_SPAN | PZXL-00173-N0006 | PZXL-00173-N0097 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0150 | PHYSICAL_SPAN | PZXL-00173-N0148 | PZXL-00173-N0149 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0151 | PHYSICAL_SPAN | PZXL-00173-N0137 | PZXL-00173-N0138 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0152 | PHYSICAL_SPAN | PZXL-00173-N0002 | PZXL-00173-N0003 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0153 | PHYSICAL_SPAN | PZXL-00173-N0007 | PZXL-00173-N0008 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0154 | PHYSICAL_SPAN | PZXL-00173-N0140 | PZXL-00173-N0141 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0155 | PHYSICAL_SPAN | PZXL-00173-N0037 | PZXL-00173-N0038 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0156 | PHYSICAL_SPAN | PZXL-00173-N0004 | PZXL-00173-N0005 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0157 | PHYSICAL_SPAN | PZXL-00173-N0144 | PZXL-00173-N0145 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0158 | PHYSICAL_SPAN | PZXL-00173-N0018 | PZXL-00173-N0019 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0159 | PHYSICAL_SPAN | PZXL-00173-N0029 | PZXL-00173-N0030 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0160 | PHYSICAL_SPAN | PZXL-00173-N0008 | PZXL-00173-N0009 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0161 | PHYSICAL_SPAN | PZXL-00173-N0021 | PZXL-00173-N0022 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0162 | PHYSICAL_SPAN | PZXL-00173-N0032 | PZXL-00173-N0033 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0163 | PHYSICAL_SPAN | PZXL-00173-N0034 | PZXL-00173-N0035 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0164 | PHYSICAL_SPAN | PZXL-00173-N0009 | PZXL-00173-N0010 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0165 | PHYSICAL_SPAN | PZXL-00173-N0145 | PZXL-00173-N0146 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0166 | PHYSICAL_SPAN | PZXL-00173-N0233 | PZXL-00173-N0234 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0167 | PHYSICAL_SPAN | PZXL-00173-N0035 | PZXL-00173-N0036 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0168 | PHYSICAL_SPAN | PZXL-00173-N0097 | PZXL-00173-N0007 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0169 | PHYSICAL_SPAN | PZXL-00173-N0039 | PZXL-00173-N0040 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0170 | PHYSICAL_SPAN | PZXL-00173-N0142 | PZXL-00173-N0143 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0171 | PHYSICAL_SPAN | PZXL-00173-N0139 | PZXL-00173-N0140 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0172 | PHYSICAL_SPAN | PZXL-00173-N0023 | PZXL-00173-N0024 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0173 | PHYSICAL_SPAN | PZXL-00173-N0043 | PZXL-00173-N0098 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0174 | PHYSICAL_SPAN | PZXL-00173-N0031 | PZXL-00173-N0032 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0175 | PHYSICAL_SPAN | PZXL-00173-N0231 | PZXL-00173-N0232 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0176 | PHYSICAL_SPAN | PZXL-00173-N0106 | PZXL-00173-N0107 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0177 | PHYSICAL_SPAN | PZXL-00173-N0056 | PZXL-00173-N0057 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0178 | PHYSICAL_SPAN | PZXL-00173-N0068 | PZXL-00173-N0069 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0179 | PHYSICAL_SPAN | PZXL-00173-N0234 | PZXL-00173-N0238 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0180 | PHYSICAL_SPAN | PZXL-00173-N0073 | PZXL-00173-N0074 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0181 | PHYSICAL_SPAN | PZXL-00173-N0227 | PZXL-00173-N0228 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0182 | PHYSICAL_SPAN | PZXL-00173-N0082 | PZXL-00173-N0128 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0183 | PHYSICAL_SPAN | PZXL-00173-N0230 | PZXL-00173-N0231 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0184 | PHYSICAL_SPAN | PZXL-00173-N0051 | PZXL-00173-N0052 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0185 | PHYSICAL_SPAN | PZXL-00173-N0055 | PZXL-00173-N0056 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0186 | PHYSICAL_SPAN | PZXL-00173-N0054 | PZXL-00173-N0055 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0187 | PHYSICAL_SPAN | PZXL-00173-N0128 | PZXL-00173-N0129 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0188 | PHYSICAL_SPAN | PZXL-00173-N0104 | PZXL-00173-N0105 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0189 | PHYSICAL_SPAN | PZXL-00173-N0052 | PZXL-00173-N0053 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0190 | PHYSICAL_SPAN | PZXL-00173-N0075 | PZXL-00173-N0076 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0191 | PHYSICAL_SPAN | PZXL-00173-N0084 | PZXL-00173-N0085 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0192 | PHYSICAL_SPAN | PZXL-00173-N0083 | PZXL-00173-N0084 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0193 | PHYSICAL_SPAN | PZXL-00173-N0107 | PZXL-00173-N0108 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0194 | PHYSICAL_SPAN | PZXL-00173-N0069 | PZXL-00173-N0070 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0195 | PHYSICAL_SPAN | PZXL-00173-N0057 | PZXL-00173-N0058 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0196 | PHYSICAL_SPAN | PZXL-00173-N0094 | PZXL-00173-N0095 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0197 | PHYSICAL_SPAN | PZXL-00173-N0105 | PZXL-00173-N0106 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0198 | PHYSICAL_SPAN | PZXL-00173-N0048 | PZXL-00173-N0049 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0199 | PHYSICAL_SPAN | PZXL-00173-N0078 | PZXL-00173-N0100 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0200 | PHYSICAL_SPAN | PZXL-00173-N0092 | PZXL-00173-N0093 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0201 | PHYSICAL_SPAN | PZXL-00173-N0076 | PZXL-00173-N0077 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0202 | PHYSICAL_SPAN | PZXL-00173-N0100 | PZXL-00173-N0101 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0203 | PHYSICAL_SPAN | PZXL-00173-N0060 | PZXL-00173-N0061 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0204 | PHYSICAL_SPAN | PZXL-00173-N0070 | PZXL-00173-N0071 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0205 | PHYSICAL_SPAN | PZXL-00173-N0090 | PZXL-00173-N0091 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0206 | PHYSICAL_SPAN | PZXL-00173-N0089 | PZXL-00173-N0090 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0207 | PHYSICAL_SPAN | PZXL-00173-N0047 | PZXL-00173-N0048 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0208 | PHYSICAL_SPAN | PZXL-00173-N0049 | PZXL-00173-N0050 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0209 | PHYSICAL_SPAN | PZXL-00173-N0087 | PZXL-00173-N0088 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0210 | PHYSICAL_SPAN | PZXL-00173-N0238 | PZXL-00173-N0239 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0211 | PHYSICAL_SPAN | PZXL-00173-N0129 | PZXL-00173-N0130 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0212 | PHYSICAL_SPAN | PZXL-00173-N0102 | PZXL-00173-N0103 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0213 | PHYSICAL_SPAN | PZXL-00173-N0066 | PZXL-00173-N0067 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0214 | PHYSICAL_SPAN | PZXL-00173-N0088 | PZXL-00173-N0089 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0215 | PHYSICAL_SPAN | PZXL-00173-N0080 | PZXL-00173-N0081 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0216 | PHYSICAL_SPAN | PZXL-00173-N0074 | PZXL-00173-N0075 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0217 | PHYSICAL_SPAN | PZXL-00173-N0081 | PZXL-00173-N0082 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0218 | PHYSICAL_SPAN | PZXL-00173-N0085 | PZXL-00173-N0086 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0219 | PHYSICAL_SPAN | PZXL-00173-N0050 | PZXL-00173-N0051 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0220 | PHYSICAL_SPAN | PZXL-00173-N0095 | PZXL-00173-N0096 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0221 | PHYSICAL_SPAN | PZXL-00173-N0062 | PZXL-00173-N0063 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0222 | PHYSICAL_SPAN | PZXL-00173-N0058 | PZXL-00173-N0059 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0223 | PHYSICAL_SPAN | PZXL-00173-N0101 | PZXL-00173-N0102 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0224 | PHYSICAL_SPAN | PZXL-00173-N0086 | PZXL-00173-N0087 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0225 | PHYSICAL_SPAN | PZXL-00173-N0053 | PZXL-00173-N0054 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0226 | PHYSICAL_SPAN | PZXL-00173-N0082 | PZXL-00173-N0083 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0227 | PHYSICAL_SPAN | PZXL-00173-N0065 | PZXL-00173-N0066 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0228 | PHYSICAL_SPAN | PZXL-00173-N0079 | PZXL-00173-N0080 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0229 | PHYSICAL_SPAN | PZXL-00173-N0130 | PZXL-00173-N0131 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0230 | PHYSICAL_SPAN | PZXL-00173-N0067 | PZXL-00173-N0068 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0231 | PHYSICAL_SPAN | PZXL-00173-N0093 | PZXL-00173-N0094 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0232 | PHYSICAL_SPAN | PZXL-00173-N0103 | PZXL-00173-N0104 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0233 | PHYSICAL_SPAN | PZXL-00173-N0061 | PZXL-00173-N0062 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0234 | PHYSICAL_SPAN | PZXL-00173-N0063 | PZXL-00173-N0064 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0235 | PHYSICAL_SPAN | PZXL-00173-N0091 | PZXL-00173-N0092 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0236 | PHYSICAL_SPAN | PZXL-00173-N0064 | PZXL-00173-N0065 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0237 | PHYSICAL_SPAN | PZXL-00173-N0078 | PZXL-00173-N0073 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00173-B0238 | PHYSICAL_SPAN | PZXL-00173-N0136 | PZXL-00173-N0137 | PZXL-00173 | CLOSED | CLOSED | YES | 60 | JKLYJ/Q-10-240 | R_X_IMAX_PENDING | 邳州_10kV河镇线明细.xlsx
PZXL-00099-SW-R004 | 分段开关 | PZXL-00099-N0007 | PZXL-00099-N0008 | R004 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认开关设备导致结构化表断边
PZXL-00097-SW-R009 | 分段开关 | PZXL-00097-N0067 | PZXL-00097-N0068 | R009 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认23/24之间存在开关
PZXL-00154-SW-R013 | 分段开关 | PZXL-00154-N0040 | PZXL-00154-N0192 | R013 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸支持；含raw名称纠正
PZXL-00154-SW-R014 | 分段开关 | PZXL-00154-N0074 | PZXL-00154-N0080 | R014 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸支持主干开关连接
PZXL-00161-SW-R016 | 分段开关 | PZXL-00161-N0036 | PZXL-00161-N0037 | R016 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认
PZXL-00161-SW-R017 | 分段开关 | PZXL-00161-N0042 | PZXL-00161-N0043 | R017 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认
PZXL-00161-SW-R018 | 分段开关 | PZXL-00161-N0043 | PZXL-00161-N0044 | R018 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认三遥开关
PZXL-00173-SW-R021 | 分段开关 | PZXL-00173-N0071 | PZXL-00173-N0072 | R021 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认
PZXL-00161-SW-R020A | BRANCH_BOX_LINK | PZXL-00161-N0043 | PZXL-00161-V001 | R020 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸：hpao 43附近分支箱链；具体内部设备连接按拓扑等值，不赋予线路长度
PZXL-00161-SW-R020B | DEVICE_LINK | PZXL-00161-V001 | PZXL-00161-V002 | R020 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸确认王场湖支线分支开关位于分支箱侧；内部长度未知按零长度设备连接
PZXL-00161-SW-R020C | BRANCH_SWITCH | PZXL-00161-V002 | PZXL-00161-N0072 | R020 | NEED_CONFIRM | CLOSED | YES | 0 | DEVICE_ZERO_LENGTH | TOPOLOGY_ONLY | 图纸明确标注“hpao线王场湖支线1分支开关（三遥）”
TIE-001 | TIE | NEED_CONFIRM | PZXL-00154-N0105 | TIE-001 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮结构化现场记录双侧闭环；当前图纸/V2对应王场湖支线17↔河东93
TIE-002 | TIE | PZXL-00092-N0146 | PZXL-00161-N0059 | TIE-002 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮结构化现场记录双侧闭环；当前V2两侧路径均可达
TIE-003 | TIE | PZXL-00097-N0187 | PZXL-00161-N0072 | TIE-003 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 双侧记录；当前V2确认联络，hpao侧需R020设备链修复
TIE-004 | TIE | NEED_CONFIRM | NEED_CONFIRM | TIE-004 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮单侧现场记录；当前V2未形成闭环，保留为待复核候选
TIE-005 | TIE | NEED_CONFIRM | NEED_CONFIRM | TIE-005 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮双侧近似记录；当前V2对应智能制造产业园开闭所母联/双电源迹象
TIE-006 | TIE | NEED_CONFIRM | NEED_CONFIRM | TIE-006 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮双侧近似记录；当前新图纸需重新落位
TIE-007 | TIE | PZXL-00154-N0193 | PZXL-00173-N0047 | TIE-007 | CLOSED | CLOSED | YES | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮正常状态已确认合闸；当前V2双侧图纸完全对应
TIE-008 | TIE | NEED_CONFIRM | NEED_CONFIRM | TIE-008 | OPEN | OPEN | NO | 0 | TIE_SWITCH | TOPOLOGY_ONLY | 上一轮双侧记录且正常分闸；当前V2未单列，保留防止与TIE-007重复计入

## 26_alias_mapping
raw_aliases | canonical_alias | canonical_name | PZXL_ID | scope | status | note
dzhen | dzhen | 墩振线 | PZXL-00099 | IN_SCOPE | CONFIRMED | 不得与dzheng混淆
dnan | dnan | 墩南线 | PZXL-00092 | IN_SCOPE | CONFIRMED | 原记录若出现“敦南线”统一纠正为墩南线
dxi / xi / d西线 | dxi | 墩西线 | PZXL-00097 | IN_SCOPE | CONFIRMED | 短别名统一dxi
hdong | hdong | 河东线 | PZXL-00154 | IN_SCOPE | CONFIRMED
hpao | hpao | 河炮线 | PZXL-00161 | IN_SCOPE | CONFIRMED | 不得与dpao混淆
hzhen | hzhen | 河镇线 | PZXL-00173 | IN_SCOPE | CONFIRMED_PROJECT_RULE | 若旧表出现“河振线”仍映射到河镇线，但保留raw
shui / dshui | dshui | 墩水线 | PZXL-00095 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
long / dlong | dlong | 墩龙线 | PZXL-00090 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
gong / dgong | dgong | 墩工线 | PZXL-00083 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dyang | dyang | 墩阳线 | PZXL-00098 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dhong | dhong | 墩红线 | PZXL-00086 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dheng | dheng | 墩恒线 | PZXL-00085 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dzheng | dzheng | 墩正线 | PZXL-00100 | BOUNDARY_ONLY | CONFIRMED | 与dzhen=PZXL-00099不同
dfan | dfan | 墩范线 | PZXL-00082 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dsong | dsong | 墩宋线 | PZXL-00096 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
dpao | dpao | 墩炮线 | PZXL-00093 | BOUNDARY_ONLY | CONFIRMED | 与hpao=PZXL-00161不同
mdong | mdong | 庙东线 | PZXL-00189 | BOUNDARY_ONLY | CONFIRMED | 不展开建模
mhui | mhui | 庙汇线 | PZXL-00198 | BOUNDARY_ONLY | CONFIRMED | 不展开建模

## 27_legacy_extract_plan
task_id | source | target | status | result | output_file | note
L001 | SRC06 邳州10kV线路基础数据表 | 六条PZXL | COMPLETED | 已提取P/I/最大允许电流/长度/半径/起点站码 | feeder_master.csv | hdong P=0已进入异常处理
L002 | SRC06 起点电站代号 | 河东/河炮/河镇 | COMPLETED | 三条均=BDZ-00048 | feeder_master.csv | 河湾站ID锁定
L003 | SRC01 变电站1 | BDZ-00027/BDZ-00048 | COMPLETED | 站容量及2025最大/最小负荷已提取 | station_boundary_2025.csv
L004 | SRC02 主变1 + 110kV设备明细 | 两站四台主变 | COMPLETED | 容量/年度极值/接线/N-1等已提取 | transformer_boundary_2025.csv
L005 | 光伏装机.xlsx | 两站2026高PV锚点 | COMPLETED | 4条主变级典型记录已提取 | station_pv_anchors_2026.csv | 不同时刻不可求和

## 28_switch_state_fusion
object_id | object_type | feeder_or_scope | locator | manual_status | manual_status_source | drawing_symbol_fill | drawing_inferred_status | final_normal_status | confidence | can_auto_apply | required_action
TIE-001 | TIE | 站间 | dzhen:24-13-17 ↔ hdong:93 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | HIGH | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-002 | TIE | 站间 | dnan:42-4 ↔ hpao:59 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | HIGH | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-003 | TIE | 站间 | dxi:15-37-14/WCH14 ↔ hpao:WCH1 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | MEDIUM_HIGH | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-004 | TIE | 站间 | dzhen:24-15-10-4 ↔ hzhen:待定位 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | MEDIUM | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-005 | TIE | 站内 | dzhen:15-14 ↔ dxi:15-15-2附近 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | MEDIUM | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-006 | TIE | 站内 | dnan:26-5附近 ↔ dxi:15-31-4附近 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | MEDIUM | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-007 | TIE | 站内 | hdong:48 ↔ hzhen:49 | CLOSED | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | CLOSED | HIGH | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
TIE-008 | TIE | 站内 | hdong:56-1附近 ↔ hzhen:56 | OPEN | 上一轮人工补录/标准化V2 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | OPEN | HIGH | YES | 人工状态为主；图纸符号只做交叉校验，不因符号识别结果覆盖人工确认状态
PZXL-00099-SW-R004 | SECTIONAL_OR_DEVICE | dzhen | dzhen线07杆 ↔ dzhen线08杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00097-SW-R009 | SECTIONAL_OR_DEVICE | dxi | dxi线23杆 ↔ dxi线24杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00154-SW-R013 | SECTIONAL_OR_DEVICE | hdong | hdong线41杆 ↔ hdong线42杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00154-SW-R014 | SECTIONAL_OR_DEVICE | hdong | hdong线73杆 ↔ hdong线74杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R016 | SECTIONAL_OR_DEVICE | hpao | hpao线36杆 ↔ hpao线37杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R017 | SECTIONAL_OR_DEVICE | hpao | hpao线42杆 ↔ hpao线43杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R018 | SECTIONAL_OR_DEVICE | hpao | hpao线43杆 ↔ hpao线44杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00173-SW-R021 | SECTIONAL_OR_DEVICE | hzhen | 10kVhzhen线73#杆 ↔ 10kVhzhen线74#杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R020A | SECTIONAL_OR_DEVICE | hpao | hpao线43杆 ↔ VIRTUAL::hpao线2分支箱 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | MEDIUM_HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R020B | SECTIONAL_OR_DEVICE | hpao | VIRTUAL::hpao线2分支箱 ↔ VIRTUAL::hpao线王场湖支线1分支开关 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | MEDIUM_HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核
PZXL-00161-SW-R020C | SECTIONAL_OR_DEVICE | hpao | VIRTUAL::hpao线王场湖支线1分支开关 ↔ hpao线王场湖支线1杆 | NOT_COVERED | 上一轮未覆盖全部普通分段开关 | PENDING_IMAGE_REVIEW | PENDING_CALIBRATION | PENDING_SYMBOL_CALIBRATION | HIGH | NO | 先用已知OPEN/CLOSED联络反标黑/空白图例；图例一致后可批量推断，实际被选为切分点的开关需正式复核

## 29_drawing_symbol_legend
calibration_id | anchor_object | known_status | drawing_locator | symbol_fill_observed | candidate_semantics | calibration_result | rule_for_agent
CAL-01 | TIE-007 | CLOSED | hdong 48 ↔ hzhen 49 | PENDING_IMAGE_REVIEW | 黑/空白二选一 | PENDING | 这是唯一已确认CLOSED高置信锚点，必须优先定位
CAL-02 | TIE-002 | OPEN | dnan 42-4 ↔ hpao 59 | PENDING_IMAGE_REVIEW | 黑/空白二选一 | PENDING | 高置信OPEN锚点
CAL-03 | TIE-001 | OPEN | dzhen 24-13-17 ↔ hdong 93 | PENDING_IMAGE_REVIEW | 黑/空白二选一 | PENDING | 高置信OPEN锚点；dzhen侧节点挂接尚需拓扑修复但状态已确认
CAL-04 | TIE-003 | OPEN | dxi WCH14 ↔ hpao WCH1 | PENDING_IMAGE_REVIEW | 黑/空白二选一 | PENDING | 中高置信OPEN锚点
CAL-RULE | 全图例 | N/A | 六张图纸 | N/A | 仅当≥1个CLOSED锚点与≥3个OPEN锚点表现出完全一致的两类填充语义时，才建立全局图例 | PENDING | 若任一锚点冲突，则禁止全局推广，改为逐开关人工核验

## 30_conductor_request
raw_model | normalized_model | r_pf_ohm_per_km | x_pf_ohm_per_km | imax_base_a | imax_upper_ref_a | parameter_grade | status | remaining_note
JKLGYJ-240 | JKLGYJ-10-240/30 | 0.13 | 0.356 | 500 | 550 | B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JKLGYJ-70 | JKLGYJ-10-70/10 | 0.443 | 0.397 | 245 | 247.5 | B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JKLYJ-150 | JKLYJ-10-150 | 0.26368 | 0.29584 | 285 | 400 | A/B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JKLYJ-240/10 | JKLYJ-10-240 (raw写法与典型库JKLYJ-240/10等价) | 0.13 | 0.356 | 500 | 550 | A/B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JKLYJ/Q-10-240 | JKLYJ/Q-10-240 | 0.13 | 0.356 | 500 | 550 | B+ | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JKLYJ/QN-10-240 | JKLYJ/QN-10-240 | 0.13 | 0.356 | 500 | 550 | B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JL(GD)/GIA-240/40 | JL(GD)/G1A-240/40 | 0.1232 | 0.356 | 550 | 595.22 | B | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JL/G1A-240/30 | JL/G1A-240/30 | 0.13 | 0.356 | 550 | 562 | B+ | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JLB3-35 | JLB3-35 (疑似地线/铝包钢类，不应作为10kV相导线瓶颈) | 0.1232 | 0.356 | 550 | 595.22 | C-PROXY | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
JLRX/T-120/30 | JLRX/T-120/30 (碳纤维复合芯耐热导线家族) | 0.33 | 0.38 | 300 | 350 | C-PROXY | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行
LGJ-10-240 | LGJ-240/30 ≈ JL/G1A-240/30 | 0.13 | 0.356 | 550 | 562 | B+ | RESOLVED_BY_PUBLIC_RESEARCH | 若C-PROXY成为瓶颈则复核；B级关键主干按给定敏感性范围运行

## 31_data_readiness
data_item | current_status | source | model_usage | remaining_gap
六条馈线→站点映射 | READY | 既有人工确认 + SRC06起点站码 | 三条墩集馈线→BDZ-00027；三条河湾馈线→BDZ-00048 | NONE
六线2025馈线边界 | READY | SRC06 | P/I/最大允许电流/长度/半径 | hdong P异常已代理并做PF敏感性
站/主变边界 | READY | SRC01/SRC02+设备明细 | 站级容量与N-1筛查 | NONE for station-aggregated case
线路R/X/Imax | READY_PLANNING | V5公开参数库+SRC06 | effective rate取较小值 | C-PROXY若成为瓶颈再复核
节点负荷 | READY_PLANNING_SEED | 旧现场容量观察 | kVA权重→馈线P闭合 | 仅需空间敏感性
节点PV | SCENARIO_READY | 现场记录+V5汇总 | 节点/馈线总量+PV factor | dnan完整装机总量未知但有7.34MW峰值出力锚点
关键联络状态 | READY | 上一轮人工确认 | 7 OPEN + TIE-007 CLOSED | 普通分段开关按图纸校准
运行场景 | READY | 真实极值锚点+规划敏感性 | S1/S2/S3 | 无同步SCADA时不称历史同步断面
馈线→母线段→具体主变 | OPTIONAL_REFINEMENT | 当前资料未明确 | 当前站级等值源端模型不需要 | 仅单台主变级N-1归因时才需要

## 32_key_path_params
tie_id | side | feeder_alias | path_status | nominal_path_km | dominant_conductor | dominant_length_km | parameter_grade | imax_base_a | imax_upper_ref_a | thermal_base_mva | thermal_upper_mva | interpretation
TIE-002 | 墩集侧 | dnan | READY | 2.25 | JKLYJ/Q-10-240 | 2.25 | B+ | 500 | 550 | 8.6603 | 9.5263 | 首个案例整条源端→联络点路径均为240绝缘主干；导线热限敏感性约8.66~9.53 MVA
TIE-002 | 河湾侧 | hpao | READY | 2.75 | LGJ-10-240→LGJ-240/30 | 2.75 | B+ | 550 | 562 | 9.5263 | 9.7341 | 55个物理档距均为LGJ-10-240；按240/30映射。热限约9.53~9.73 MVA
TIE-003 | 墩集侧 | dxi | READY_DEBUG_TOPOLOGY | 3.25 | JKLYJ/Q-10-240 | 3.25 | B+ | 500 | 550 | 8.6603 | 9.5263 | 源端→王场湖支线14现有物理路径全部为240绝缘导线
TIE-003 | 河湾侧 | hpao | READY_WITH_R020_DEBUG_CHAIN | 2 | LGJ-10-240→LGJ-240/30 | 2 | B+ | 550 | 562 | 9.5263 | 9.7341 | 物理档距均为LGJ-10-240，另含R020零长度设备链
TIE-001 | 河湾侧 | hdong | BLOCKED_BY_EXISTING_TOPOLOGY_GAPS |  | 预计以JL(GD)/G1A-240/40为主 |  | B | 550 | 595.22 | 9.5263 | 10.3095 | 先闭环hdong R010~R014，再重新统计真实源端→93路径

## 33_conductor_sources
source_id | source_type | use | key_fact | url | reliability_note
S01 | 国家标准 | JKLYJ/JKLGYJ族标准归属 | GB/T 14049-2008现行：额定电压10kV架空绝缘电缆 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=498F0E9BDCC9F878D7A6272E0AEC46AD | A
S02 | 国家标准 | JL/G1A等裸架空导线标准归属 | GB/T 1179-2017现行：圆线同心绞架空导线 | https://openstd.samr.gov.cn/bzgk/std/newGbInfo?hcno=F936B58052E9B750D1FEF196B660A084 | A
S03 | 发明专利技术实施例 | 10kV潮流典型R/X/I | JKLYJ-240/10: 0.13+j0.356 Ω/km, 500A；JKLYJ-150:0.26368+j0.295839341,285A | https://patents.google.com/patent/CN116581754A/zh | A-典型参数库，不等同具体资产出厂值
S04 | 政府公开配网开放容量 | 10kV运营载流量参考 | JKLGYJ-240约550A、JKLGYJ-70约245A；另有JKLYJ型号限额 | https://upload.xuancheng.gov.cn/download?id=693357&siteId=6 | A-实际配网限额口径
S05 | 政府公开配网开放容量 | 10kV运营载流量参考 | JKLYJ-240约550A、JKLYJ-150约400A | https://upload.xuancheng.gov.cn/download?id=648384&siteId=3 | A-实际配网限额口径
S06 | 政府工程 | JKLGYJ型号规范化 | 10kV工程采用JKLGYJ-10-240/30 | https://ggzy.ht.gov.cn/jyxx/001004/001004001/20260610/45de60d1-eae9-46a8-8704-cc5323d3b243.html | A
S07 | 政府工程 | JKLGYJ型号规范化 | 10kV工程采用JKLGYJ-10-70/10 | https://www.jl.gov.cn/ggzy/sysggzy/sysjyxx/sysgcjs/ccsgczbgg/202605/t20260528_9636242.html | A
S08 | 研究论文 | 高导电率JL(GD)/G1A-240/40 | 20℃Rdc=0.1171Ω/km；示例交流R=0.1232Ω/km | https://pdf.hanspub.org/tdet20200200000_87962235.pdf | B+ 原始研究参数
S09 | 政府环评/可研参数 | JL/G1A-240/40载流量 | 允许载流量595.22A（给定工程条件） | https://hbj.yzcity.gov.cn/hbj/031005/202506/f53fbe5f8fab47c696d9720a7c11fad6/files/dd041c21d3304b01a96e41ee0fa8e614.pdf | A-条件相关
S10 | 政府环评/设计参数 | JL/G1A-240/30电阻 | 20℃直流电阻0.1181Ω/km | https://sthjj.huhhot.gov.cn/ywgz/hjyxpj/xmslqk/202511/P020251127380578958416.pdf | A
S11 | 政府环评/可研参数 | LGJ-240/30载流量 | 562A/相（环境40℃、线温80℃） | https://sthjj.quanzhou.gov.cn/hjgl/hbsp/hpslqkgk/202606/P020260618423129515361.pdf | A-条件明确
S12 | 国家公共资源项目 | LGJ-10-240命名映射 | 10kV架空工程采用LGJ-240/30 | https://www.ggzy.gov.cn/information/deal/html/b/0067/0101/20260604/00679edf62f7e5a847868b19d27564377738.html | A
S13 | 发明专利 | JLRX/T族识别 | JLRX/T属于碳纤维复合芯耐热导线家族 | https://patents.google.com/patent/CN105529651A/zh | A-家族确认，非120/30精确参数

## 34_station_boundary
station_id | station_name | rated_capacity_mva | 2025_annual_max_load_mw | max_time | 2025_annual_min_load_mw | min_time | normal_spare_at_annual_max_mva | main_wiring | 10kv_intervals_total | 10kv_intervals_remaining | n1_flag_from_asset_table | transformer_count | largest_transformer_mva | surviving_capacity_after_largest_outage_mva | simple_n1_screening_gap_at_station_peak_mw | expandable_transformer_count | expandable_capacity_mva | boundary_use_rule | source
BDZ-00027 | 墩集变 | 100 | 59.21 | 2025-08-29 17:00:00 | -37.27 | 2025-05-01 11:47:00 | 40.79 | 单母分段 | 24 | 0 | 是 | 2 | 50 | 50 | -9.21 | 1 | 50 | simple N-1 gap仅容量筛查，实际N-1需10kV/上级网络转供联合校核。 | 数据_脱敏(1).zip: 2025设备负载统计表+110（35）kv设备明细
BDZ-00048 | 河湾变 | 150 | 73.74 | 2025-07-05 22:10:00 | -5.22 | 2025-04-22 12:35:00 | 76.26 | 单母分段 | 26 | 0 | 是 | 2 | 100 | 50 | -23.74 | 1 | 100 | simple N-1 gap仅容量筛查，实际N-1需10kV/上级网络转供联合校核。 | 数据_脱敏(1).zip: 2025设备负载统计表+110（35）kv设备明细

## 35_transformer_boundary
station_id | station_name | transformer_id | rated_mva | 2025_max_load_mw | max_load_pct | max_time | 2025_min_load_mw | min_load_pct | min_time | special_operation_note | n1_flag | hv_switchgear | mv_switchgear | capacitor_kvar | neutral_grounding | upstream_station_id | source
BDZ-00027 | 墩集变 | #2 | 50 | 42.34 | 84.68 | 2025-04-02 18:49:00 | -12.31 | -24.62 | 2025-04-02 12:11:00 | 非正常运行状态，另一台主变停运 | 是 | GIS | 开关柜 | 9008 | 经消弧线圈接地 | BDZ-00199 | 数据_脱敏(1).zip: 主变1+设备明细
BDZ-00027 | 墩集变 | #3 | 50 | 41.34 | 82.68 | 2025-04-01 18:20:00 | -31.85 | -63.7 | 2025-05-03 12:40:00 | 非正常运行状态，另一台主变停运 | 是 | GIS | 开关柜 | 8400 | 经消弧线圈接地 | BDZ-00199 | 数据_脱敏(1).zip: 主变1+设备明细
BDZ-00048 | 河湾变 | #1 | 100 | 51.91 | 51.91 | 2025-07-05 21:40:00 | -2.61 | -2.61 | 2025-03-22 12:45:00 |  | 是 | AIS | 开关柜 | 24000 | 经消弧线圈接地 | BDZ-00238 | 数据_脱敏(1).zip: 主变1+设备明细
BDZ-00048 | 河湾变 | #2 | 50 | 41.73 | 83.46 | 2025-08-06 22:10:00 | -4.42 | -8.84 | 2025-04-29 13:30:00 | 特殊运行方式，2号主变切带1号主变负荷 | 是 | AIS | 开关柜 | 20424 | 经消弧线圈接地 | BDZ-00199 | 数据_脱敏(1).zip: 主变1+设备明细

## 36_station_pv_anchors
feeder_id | feeder_alias | node_id | node_name | pv_capacity_kva_seed | location_quality | scenario_pg_rule | source | note
数据_脱敏(1).zip: 光伏装机.xlsx
数据_脱敏(1).zip: 光伏装机.xlsx
数据_脱敏(1).zip: 光伏装机.xlsx
数据_脱敏(1).zip: 光伏装机.xlsx

## 37_asset_obs_seed
feeder_id | feeder_alias | raw_locator | asset_type | capacity_kva | mapped_node_id | mapped_node_name | mapping_method | mapping_confidence | observation_confidence | raw_note | source
PZXL-00092 | dnan | 22 | LOAD_TRANSFORMER_KVA | 2000 | PZXL-00092-N0042 | dnan线22杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 28 | LOAD_TRANSFORMER_KVA | 2000 | PZXL-00092-N0048 | dnan线28杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 28-14 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00092-N0048 | dnan线28杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 28-16 | LOAD_TRANSFORMER_KVA | 110 | PZXL-00092-N0048 | dnan线28杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 28-17 | LOAD_TRANSFORMER_KVA | 160 | PZXL-00092-N0048 | dnan线28杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 28-18 | LOAD_TRANSFORMER_KVA | 20 | PZXL-00092-N0048 | dnan线28杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 42-3 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00092-N0062 | dnan线42杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 46-2 | LOAD_TRANSFORMER_KVA | 200 | PZXL-00092-N0067 | dnan线46-2 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 49 | LOAD_TRANSFORMER_KVA | 4100 | PZXL-00092-N0071 | dnan线49杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 64-4 | LOAD_TRANSFORMER_KVA | 3000 | PZXL-00092-N0095 | dnan线64杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 73-4 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00092-N0109 | dnan线73-4 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 73-6 | LOAD_TRANSFORMER_KVA | 160 | PZXL-00092-N0111 | dnan线73-6 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 73-11 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00092-N0106 | dnan线73-11 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 73-4 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00092-N0109 | dnan线73-4 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 73-4 | LOAD_TRANSFORMER_KVA | 500 | PZXL-00092-N0109 | dnan线73-4 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 83-6 | LOAD_TRANSFORMER_KVA | 200 | PZXL-00092-N0126 | dnan线83杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 83-15 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00092-N0126 | dnan线83杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-5 | LOAD_TRANSFORMER_KVA | 315 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-9-2 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-11 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-12 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-13 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-13 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 90-5 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00092-N0133 | dnan线90杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 101 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00092-N0027 | dnan线101杆 | EXACT_CURRENT_NODE | HIGH | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00092 | dnan | 21 | PV_CAPACITY_KVA | 250 | PZXL-00092-N0041 | dnan线21杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | MEDIUM | 现场可确认的一处250kVA光伏；全馈线装机仍不完整 | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 19 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0019 | dzhen线19杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 15-1 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00099-N0015 | dzhen线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 15-1 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0015 | dzhen线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-6 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-8 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-10 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-13 | LOAD_TRANSFORMER_KVA | 30 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-17 | LOAD_TRANSFORMER_KVA | 2700 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-22 | LOAD_TRANSFORMER_KVA | 400 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-23 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-24 | LOAD_TRANSFORMER_KVA | 315 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-15-17 | LOAD_TRANSFORMER_KVA | 610 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 33-1 | LOAD_TRANSFORMER_KVA | 630 | PZXL-00099-N0034 | dzhen线33杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-15-10-10 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-15-n4 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 7 | PV_CAPACITY_KVA | 250 | PZXL-00099-N0007 | dzhen线07杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 15-3 | PV_CAPACITY_KVA | 2500 | PZXL-00099-N0015 | dzhen线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-4 | PV_CAPACITY_KVA | 500 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-15-10-2 | PV_CAPACITY_KVA | 200 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | 24-15-10-10 | PV_CAPACITY_KVA | 3150 | PZXL-00099-N0024 | dzhen线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi |  | LOAD_TRANSFORMER_KVA | 220 | PZXL-00097-N0044 | dxi线01杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 6-13 | LOAD_TRANSFORMER_KVA | 200 | PZXL-00097-N0049 | dxi线06杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-3 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-11 | LOAD_TRANSFORMER_KVA | 200 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-37-4 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-37-6 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-37-7 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-37-9 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-15-2 | LOAD_TRANSFORMER_KVA | 5530 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 24-17 | LOAD_TRANSFORMER_KVA | 2600 | PZXL-00097-N0068 | dxi线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 6-15 | PV_CAPACITY_KVA | 200 | PZXL-00097-N0049 | dxi线06杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 15-15-2 | PV_CAPACITY_KVA | 2500 | PZXL-00097-N0059 | dxi线15杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | 44-6 | PV_CAPACITY_KVA | 200 | PZXL-00097-N0089 | dxi线44杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 1380 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 50 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 50 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 20 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 50 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong |  | LOAD_TRANSFORMER_KVA | 30 | PZXL-00154-N0016 | hdong线1杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 23-8 | LOAD_TRANSFORMER_KVA | 800 | PZXL-00154-N0020 | hdong线23杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 23-11 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00154-N0020 | hdong线23杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 23-11 | LOAD_TRANSFORMER_KVA | 630 | PZXL-00154-N0020 | hdong线23杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 24-1 | LOAD_TRANSFORMER_KVA | 30 | PZXL-00154-N0021 | hdong线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 24-2 | LOAD_TRANSFORMER_KVA | 110 | PZXL-00154-N0021 | hdong线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 24-3 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00154-N0021 | hdong线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 24-1 | LOAD_TRANSFORMER_KVA | 400 | PZXL-00154-N0021 | hdong线24杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 74-6 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00154-N0080 | hdong线74杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 74-10 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00154-N0080 | hdong线74杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 80-1-2 | LOAD_TRANSFORMER_KVA | 160 | PZXL-00154-N0091 | hdong线80杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 80-3-1 | LOAD_TRANSFORMER_KVA | 30 | PZXL-00154-N0091 | hdong线80杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | 42-7-1 | PV_CAPACITY_KVA | 1890 | PZXL-00154-N0192 | hdong线42杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | MEDIUM | 馈线总PV=1890kVA，现场描述为该区域附近4个用户，合并至父节点 | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 2 | LOAD_TRANSFORMER_KVA | 100 | PZXL-00161-N0002 | hpao线02杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 43-1 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00161-N0043 | hpao线43杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 43-1 | LOAD_TRANSFORMER_KVA | 50 | PZXL-00161-N0043 | hpao线43杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 52-5 | LOAD_TRANSFORMER_KVA | 250 | PZXL-00161-N0052 | hpao线52杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 53-5 | LOAD_TRANSFORMER_KVA | 20 | PZXL-00161-N0053 | hpao线53杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 53-9 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00161-N0053 | hpao线53杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 53-10 | LOAD_TRANSFORMER_KVA | 80 | PZXL-00161-N0053 | hpao线53杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 53-11 | LOAD_TRANSFORMER_KVA | 330 | PZXL-00161-N0053 | hpao线53杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00161 | hpao | 53-5 | LOAD_TRANSFORMER_KVA | 1000 | PZXL-00161-N0053 | hpao线53杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen |  | LOAD_TRANSFORMER_KVA | 80 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen |  | LOAD_TRANSFORMER_KVA | 2100 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen |  | LOAD_TRANSFORMER_KVA | 160 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen |  | LOAD_TRANSFORMER_KVA | 400 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen |  | LOAD_TRANSFORMER_KVA | 400 | PZXL-00173-N0001 | 10kVhzhen线01#杆 | ROOT_FALLBACK | LOW | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-8 | LOAD_TRANSFORMER_KVA | 400 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | LOAD_TRANSFORMER_KVA | 500 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | LOAD_TRANSFORMER_KVA | 500 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | LOAD_TRANSFORMER_KVA | 3300 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | LOAD_TRANSFORMER_KVA | 630 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | LOAD_TRANSFORMER_KVA | 2000 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | HIGH |  | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00173 | hzhen | 21-5-2 | PV_CAPACITY_KVA | 2500 | PZXL-00173-N0020 | 10kVhzhen线21#杆 | PARENT_MAIN_NODE_AGGREGATION | MEDIUM | MEDIUM | 馈线总PV=2500kVA；精确拆分不可恢复，聚合到已知PV相关支路 | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS

## 38_node_load_seed
feeder_id | feeder_alias | node_id | node_name | observed_capacity_kva_aggregated | weight_within_observed_capacity | p_seed_mw_at_feeder_stress | q_seed_mvar_pf095 | allocation_method | usage_status | sensitivity_required
PZXL-00092 | dnan | PZXL-00092-N0027 | dnan线101杆 | 50 | 0.0035625 | 0.023262 | 0.0076458 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0042 | dnan线22杆 | 2000 | 0.1425 | 0.93047 | 0.30583 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0048 | dnan线28杆 | 2370 | 0.16886 | 1.1026 | 0.36241 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0062 | dnan线42杆 | 250 | 0.017813 | 0.11631 | 0.038229 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0067 | dnan线46-2 | 200 | 0.01425 | 0.093047 | 0.030583 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0071 | dnan线49杆 | 4100 | 0.29213 | 1.9075 | 0.62696 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0095 | dnan线64杆 | 3000 | 0.21375 | 1.3957 | 0.45875 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0106 | dnan线73-11 | 100 | 0.007125 | 0.046524 | 0.015292 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0109 | dnan线73-4 | 800 | 0.057 | 0.37219 | 0.12233 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0111 | dnan线73-6 | 160 | 0.0114 | 0.074438 | 0.024467 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0126 | dnan线83杆 | 250 | 0.017813 | 0.11631 | 0.038229 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00092 | dnan | PZXL-00092-N0133 | dnan线90杆 | 755 | 0.053794 | 0.35125 | 0.11545 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00097 | dxi | PZXL-00097-N0044 | dxi线01杆 | 220 | 0.023158 | 0.078593 | 0.025832 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00097 | dxi | PZXL-00097-N0049 | dxi线06杆 | 200 | 0.021053 | 0.071449 | 0.023484 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00097 | dxi | PZXL-00097-N0059 | dxi线15杆 | 6480 | 0.68211 | 2.3149 | 0.76088 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00097 | dxi | PZXL-00097-N0068 | dxi线24杆 | 2600 | 0.27368 | 0.92883 | 0.30529 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00099 | dzhen | PZXL-00099-N0015 | dzhen线15杆 | 330 | 0.051362 | 0.42293 | 0.13901 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00099 | dzhen | PZXL-00099-N0019 | dzhen线19杆 | 250 | 0.038911 | 0.3204 | 0.10531 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00099 | dzhen | PZXL-00099-N0024 | dzhen线24杆 | 5215 | 0.81167 | 6.6836 | 2.1968 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00099 | dzhen | PZXL-00099-N0034 | dzhen线33杆 | 630 | 0.098054 | 0.80742 | 0.26539 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00154 | hdong | PZXL-00154-N0016 | hdong线1杆 | 1580 | 0.39012 | 3.4957 | 1.149 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00154 | hdong | PZXL-00154-N0020 | hdong线23杆 | 1530 | 0.37778 | 3.3851 | 1.1126 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00154 | hdong | PZXL-00154-N0021 | hdong线24杆 | 620 | 0.15309 | 1.3717 | 0.45087 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00154 | hdong | PZXL-00154-N0080 | hdong线74杆 | 130 | 0.032099 | 0.28762 | 0.094538 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00154 | hdong | PZXL-00154-N0091 | hdong线80杆 | 190 | 0.046914 | 0.42037 | 0.13817 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00161 | hpao | PZXL-00161-N0002 | hpao线02杆 | 100 | 0.05102 | 0.096306 | 0.031654 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00161 | hpao | PZXL-00161-N0043 | hpao线43杆 | 100 | 0.05102 | 0.096306 | 0.031654 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00161 | hpao | PZXL-00161-N0052 | hpao线52杆 | 250 | 0.12755 | 0.24076 | 0.079135 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00161 | hpao | PZXL-00161-N0053 | hpao线53杆 | 1510 | 0.77041 | 1.4542 | 0.47798 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00173 | hzhen | PZXL-00173-N0001 | 10kVhzhen线01#杆 | 3140 | 0.2999 | 1.8864 | 0.62002 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds
PZXL-00173 | hzhen | PZXL-00173-N0020 | 10kVhzhen线21#杆 | 7330 | 0.7001 | 4.4036 | 1.4474 | NORMALIZE_OBSERVED_FIELD_KVA_TO_FEEDER_BOUNDARY_P | PLANNING_SEED | YES: compare with uniform-leaf allocation if voltage or branch flow binds

## 39_node_pv_seed
feeder_id | feeder_alias | node_id | node_name | pv_capacity_kva_seed | location_quality | scenario_pg_rule | source | note
PZXL-00092 | dnan | PZXL-00092-N0041 | dnan线21杆 | 250 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS | 现场可确认的一处250kVA光伏；全馈线装机仍不完整
PZXL-00099 | dzhen | PZXL-00099-N0007 | dzhen线07杆 | 250 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | PZXL-00099-N0015 | dzhen线15杆 | 2500 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | PZXL-00099-N0024 | dzhen线24杆 | 500 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | PZXL-00099-N0024 | dzhen线24杆 | 200 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00099 | dzhen | PZXL-00099-N0024 | dzhen线24杆 | 3150 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | PZXL-00097-N0049 | dxi线06杆 | 200 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | PZXL-00097-N0059 | dxi线15杆 | 2500 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00097 | dxi | PZXL-00097-N0089 | dxi线44杆 | 200 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS
PZXL-00154 | hdong | PZXL-00154-N0192 | hdong线42杆 | 1890 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS | 馈线总PV=1890kVA，现场描述为该区域附近4个用户，合并至父节点
PZXL-00173 | hzhen | PZXL-00173-N0020 | 10kVhzhen线21#杆 | 2500 | MEDIUM | Pg_MW=capacity_kVA/1000×pv_factor; unity-PF PV baseline | prior 01_10kV局部网架标准化输入_V2.xlsx / 05_CAPACITY_OBS or 03_RAW_CELLS | 馈线总PV=2500kVA；精确拆分不可恢复，聚合到已知PV相关支路
PZXL-00092 | dnan |  | FEEDER_LEVEL_ANCHOR |  | FEEDER_LEVEL_ONLY | 高PV场景可用总出力7.34MW作真实峰值锚点；不得解释为装机容量 | prior field observation consolidated in V5 | dnan完整PV装机容量不可由现有资料严格恢复

## 40_operating_scenarios
scenario_id | scenario_name | purpose | load_boundary_rule | pv_rule | station_boundary_rule | line_limit_rule | voltage_rule | q_rule | synchronization_status | formal_use
S0_TOPOLOGY_ONLY | 基准拓扑审计 | 正常开关状态、孤岛、环路、源端可达性 | 不要求负荷数值 | 不要求PV | 不启用 | 不启用 | 不启用 | 不启用 | N/A | YES_TOPOLOGY
S1_FEEDER_STRESS | 馈线正向应力包络 | 局部联络正向转供及热稳/电压能力 | 六线采用SRC06历史最大P；hdong用544.57A×10kV×√3×PF0.95代理；节点按现场kVA权重 | PV factor=0基准，另做0.1敏感性 | 站级容量/年度峰值作容量筛查，不宣称同一历史时刻 | min(导线Imax_base,SRC06馈线最大允许电流) | 硬0.93~1.07pu；优选0.95~1.05pu | PF0.95；0.90/0.98敏感性 | ENVELOPE_NOT_HISTORICAL_SYNCHRONOUS | PLANNING_ENVELOPE
S2_REVERSE_PV | 高PV反送应力 | 反向潮流、过电压、反向转供 | S1空间权重，load_factor=0.3/0.5/0.7 | 已知PV容量×0.8/0.9/1.0；dnan可用7.34MW峰值锚点；hpao=0 | 2025站级最小净负荷与2026PV典型记录仅作边界一致性校核 | 同S1 | 0.93~1.07pu | 负荷PF0.95；PV unity PF基准 | PLANNING_SCENARIO_WITH_REAL_ANCHORS | PLANNING_STRESS
S3_TRANSFER_SWEEP | 联络最大转供扫描 | 识别最大转供与首个绑定约束 | 分别以S1/S2基础状态扫描 | 继承基础场景 | 同时检查站端容量和N-1筛查边界 | effective_rate_a_base；另跑upper sensitivity | 0.93~1.07pu | 继承 | SCENARIO_BASED | YES_PLANNING

## 41_final_preflight
qa_id | priority | category | issue | status | impact | prepared_resolution | remaining_action
QF01 | P0 | STATION_MAPPING | 六条馈线→110kV站归属 | PASS | 局部10kV联络案例的源端边界 | 墩振/墩西/墩南→墩集变BDZ-00027；河东/河炮/河镇→河湾变BDZ-00048，已完整落库。 | NONE
QF02 | P0 | FEEDER_BOUNDARY | 六线P/I/运行限额 | PASS_WITH_ANOMALY_GUARD | 潮流/热限基础 | 六线已提取；hdong P=0与电流/负载率冲突，规划P用I×PF0.95代理。 | 如后续获得河东实际同步P，可覆盖代理值
QF03 | P0 | LINE_LIMIT | 线路/馈线运行限额 | PASS_PLANNING | 防止仅按导线Imax高估 | 1124边 effective_rate=min(导线Imax, SRC06馈线最大允许电流)。 | 某具体开关若成为绑定瓶颈，再定点核铭牌
QF04 | P0 | STATION_BOUNDARY | 墩集/河湾站及四台主变边界 | PASS | 站端源/受端能力与N-1筛查 | 墩集100MVA(50+50)、河湾150MVA(100+50)，主变容量、年度正反向极值、N-1台账已入库。 | NONE for station-aggregated 10kV case
QF05 | P0 | LOAD_SPATIAL | 节点负荷空间分布 | PASS_PLANNING_SEED | 压降/支路潮流 | 旧现场容量观察映射到当前节点；缺细分子节点时聚合至父主杆；按kVA权重闭合至馈线P。 | 若分布方式成为约束，跑uniform-leaf敏感性
QF06 | P0 | PV_SPATIAL | PV位置/容量 | PARTIAL_BUT_SCENARIO_READY | 反向潮流/电压 | dzhen已定位6600/6650kVA；hdong/hzhen总量聚合；hpao=0；dnan有7.34MW实际峰值出力锚点。 | dnan完整装机总量未知，但不阻断高PV规划场景
QF07 | P0 | SWITCH_STATE | 8处关键联络正常状态 | PASS | 基准拓扑 | 7 OPEN + TIE-007 CLOSED 已继承。 | 普通分段开关按图纸黑/空白符号校准
QF08 | P0 | TOPOLOGY | TIE-002 | PASS_FIRST_CASE | 首个规划案例 | 两侧路径、线路参数、馈线边界、节点注入种子、站端边界均已准备。 | NONE before calculation
QF09 | P1 | TOPOLOGY | TIE-001 / TIE-003局部拓扑断点 | PARTIAL | 后续两条跨站联络 | R005/R010-R014/R020已进入拓扑patch任务。 | Agent依据现有图纸闭环后计算
QF10 | P1 | SYNCHRONIZATION | 无六线同时间戳P/Q历史断面 | NO_LONGER_BLOCKS_PLANNING | 不能宣称历史真实同步断面 | 采用明确的规划包络场景，禁止把各馈线年度极值简单相加冒充同步断面。 | 后续若有SCADA同步断面可替换
QF11 | P2 | OPTIONAL_REFINEMENT | 馈线→10kV母线段→具体主变归属 | OPTIONAL_NOT_REQUIRED | 仅影响把转供结果进一步精确归因到单台主变/母线段 | 当前局部10kV案例按已确认的110kV站级等值源端建模；六线→站点映射已经完整。 | 只有后续明确要求单台主变级N-1归因时再补，不是当前缺口

## 42_load_seed_check
feeder_id | feeder_alias | boundary_p_mw | sum_node_p_seed_mw | closure_error_mw | observed_capacity_kva_sum | node_seed_count | status
PZXL-00092 | dnan | 6.5296 | 6.5296 | 1e-08 | 14035 | 12 | PASS
PZXL-00099 | dzhen | 8.2344 | 8.2344 | 0 | 6425 | 4 | PASS
PZXL-00097 | dxi | 3.3938 | 3.3938 | 1e-08 | 9500 | 4 | PASS
PZXL-00154 | hdong | 8.9606 | 8.9606 | 1e-08 | 4050 | 5 | PASS
PZXL-00161 | hpao | 1.8876 | 1.8876 | -1e-08 | 1960 | 4 | PASS
PZXL-00173 | hzhen | 6.2899 | 6.2899 | 0 | 10470 | 2 | PASS