# 2021—2025 年度容载比方案矩阵与最终推荐区间

## 口径说明

方案代码使用 SCHEME_C0/SCHEME_A/SCHEME_B，证据等级使用 EVIDENCE_A/EVIDENCE_B/EVIDENCE_C。每年分别比较仅扩容、仅配储、扩容+配储；2021为静态参考，2022—2024为诊断回放，2025为当前正式优化入口。缺少同年8760或资产/候选闭环时不填伪造EAC。容载比分母固定为干预前正向同步峰值，110/35 kV不混算。

### 2021年110 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | 2.887 | 2.633 | 2.912 | 2.838 | 2.148 | 2.252 | — | 3.589 |
| 当前推荐方案代码 | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | NOT_IDENTIFIABLE | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 1235.000 | 699.500 | 1885.500 | 2027.000 | 3113.500 | 1382.000 | 1737.000 | 1785.000 |
| 干预前正向同步峰值 P_plus_base（MW） | 427.800 | 265.650 | 647.410 | 731.770 | 1449.770 | 613.640 | 701.120 | 525.230 |
| 现状模型容载比 R0 | 2.887 | 2.633 | 2.912 | 2.770 | 2.148 | 2.252 | 2.477 | 3.399 |
| 官方历史参考容载比（仅作参考） | 2.890 | 2.630 | 2.910 | 2.770 | 2.150 | 2.250 | 2.480 | 3.400 |
| C0状态（现状不采取措施） | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | feasible / EAC=31.531 | feasible / EAC=154.276 | feasible / EAC=559.661 | feasible / EAC=1417.716 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B联合：状态 / EAC（万元/年） | feasible / EAC=31.531 | feasible / EAC=154.276 | feasible / EAC=559.661 | feasible / EAC=572.167 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | feasible / EAC=740.083 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | feasible / EAC=31.531 | feasible / EAC=154.276 | feasible / EAC=559.661 | feasible / EAC=1417.716 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | feasible / EAC=121.741 | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | feasible / EAC=31.531 | feasible / EAC=154.276 | feasible / EAC=559.661 | feasible / EAC=1417.716 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |

### 2021年110 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 1235.000 | 427.800 | 2.887 | SCHEME_B | 2.887 | 31.531 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00003 | EVIDENCE_C | 699.500 | 265.650 | 2.633 | SCHEME_B | 2.633 | 154.276 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00004 | EVIDENCE_C | 1885.500 | 647.410 | 2.912 | SCHEME_B | 2.912 | 559.661 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00005 | EVIDENCE_C | 2027.000 | 731.770 | 2.770 | SCHEME_B | 2.838 | 572.167 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00007 | EVIDENCE_C | 3113.500 | 1449.770 | 2.148 | SCHEME_B | 2.148 | 0.000 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00008 | EVIDENCE_C | 1382.000 | 613.640 | 2.252 | SCHEME_B | 2.252 | 0.000 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00009 | EVIDENCE_C | 1737.000 | 701.120 | 2.477 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00010 | EVIDENCE_C | 1785.000 | 525.230 | 3.399 | SCHEME_B | 3.589 | 740.083 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |

### 2021年35 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | — | 2.303 | — | 3.034 | — | — | 2.432 | — |
| 当前推荐方案代码 | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE |
| 同电压公用变容量 S0（MVA） | 288.800 | 326.000 | 243.000 | 245.000 | 56.000 | 185.600 | 310.300 | 287.500 |
| 干预前正向同步峰值 P_plus_base（MW） | 105.300 | 141.580 | 134.170 | 80.760 | 32.430 | 85.550 | 127.590 | 122.090 |
| 现状模型容载比 R0 | 2.743 | 2.303 | 1.811 | 3.034 | 1.727 | 2.169 | 2.432 | 2.355 |
| 官方历史参考容载比（仅作参考） | 2.740 | 2.300 | 1.810 | 3.030 | 1.730 | 2.170 | 2.430 | 2.350 |
| C0状态（现状不采取措施） | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 | not_identifiable_or_data_gap / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=838.925 | infeasible | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=615.968 | infeasible |
| 方案B联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=838.925 | infeasible | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=615.968 | infeasible |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=838.925 | infeasible | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=615.968 | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=838.925 | infeasible | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=615.968 | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |

### 2021年35 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 288.800 | 105.300 | 2.743 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00003 | EVIDENCE_C | 326.000 | 141.580 | 2.303 | SCHEME_B | 2.303 | 838.925 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00004 | EVIDENCE_C | 243.000 | 134.170 | 1.811 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00005 | EVIDENCE_C | 245.000 | 80.760 | 3.034 | SCHEME_B | 3.034 | 0.000 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00007 | EVIDENCE_C | 56.000 | 32.430 | 1.727 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00008 | EVIDENCE_C | 185.600 | 85.550 | 2.169 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00009 | EVIDENCE_C | 310.300 | 127.590 | 2.432 | SCHEME_B | 2.432 | 615.968 | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |
| QX-00010 | EVIDENCE_C | 287.500 | 122.090 | 2.355 | NOT_IDENTIFIABLE | — | — | official static anchor only; no same-year 8760, annual asset scope, PV snapshot or cost candidate closure |

### 2022年110 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | 2.669 | 2.904 | 3.118 | 2.540 | 2.335 | 2.276 | — | 3.263 |
| 当前推荐方案代码 | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | NOT_IDENTIFIABLE | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 1235.000 | 829.500 | 1955.500 | 2045.500 | 3345.000 | 1430.500 | 1807.000 | 1885.000 |
| 干预前正向同步峰值 P_plus_base（MW） | 481.402 | 285.689 | 627.197 | 825.004 | 1432.370 | 628.478 | 724.903 | 623.698 |
| 现状模型容载比 R0 | 2.565 | 2.904 | 3.118 | 2.479 | 2.335 | 2.276 | 2.493 | 3.022 |
| 官方历史参考容载比（仅作参考） | 2.570 | 2.900 | 3.120 | 2.480 | 2.340 | 2.280 | 2.490 | 3.020 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | feasible / EAC=195.938 | feasible / EAC=328.815 | feasible / EAC=367.101 | feasible / EAC=2489.731 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B联合：状态 / EAC（万元/年） | feasible / EAC=121.741 | feasible / EAC=328.815 | feasible / EAC=367.101 | feasible / EAC=1218.532 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | feasible / EAC=1807.717 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | feasible / EAC=195.938 | feasible / EAC=328.815 | feasible / EAC=367.101 | feasible / EAC=2489.731 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | feasible / EAC=121.741 | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | feasible / EAC=195.938 | feasible / EAC=328.815 | feasible / EAC=367.101 | feasible / EAC=2489.731 | feasible / EAC=0.000 | feasible / EAC=0.000 | infeasible | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2022年110 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 1235.000 | 481.402 | 2.565 | SCHEME_B | 2.669 | 121.741 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00003 | EVIDENCE_C | 829.500 | 285.689 | 2.904 | SCHEME_B | 2.904 | 328.815 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00004 | EVIDENCE_C | 1955.500 | 627.197 | 3.118 | SCHEME_B | 3.118 | 367.101 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00005 | EVIDENCE_C | 2045.500 | 825.004 | 2.479 | SCHEME_B | 2.540 | 1218.532 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00007 | EVIDENCE_C | 3345.000 | 1432.370 | 2.335 | SCHEME_B | 2.335 | 0.000 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00008 | EVIDENCE_C | 1430.500 | 628.478 | 2.276 | SCHEME_B | 2.276 | 0.000 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00009 | EVIDENCE_C | 1807.000 | 724.903 | 2.493 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00010 | EVIDENCE_C | 1885.000 | 623.698 | 3.022 | SCHEME_B | 3.263 | 1807.717 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2022年35 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | — | 2.431 | — | — | — | — | 2.943 | — |
| 当前推荐方案代码 | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE |
| 同电压公用变容量 S0（MVA） | 250.500 | 292.000 | 240.000 | 263.000 | 56.000 | 185.600 | 258.300 | 234.500 |
| 干预前正向同步峰值 P_plus_base（MW） | 115.175 | 120.132 | 103.913 | 124.718 | 11.017 | 107.396 | 87.770 | 117.617 |
| 现状模型容载比 R0 | 2.175 | 2.431 | 2.310 | 2.109 | 5.083 | 1.728 | 2.943 | 1.994 |
| 官方历史参考容载比（仅作参考） | 2.170 | 2.430 | 2.310 | 2.110 | 5.080 | 1.730 | 2.940 | 1.990 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=430.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案B联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=430.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=430.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=430.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2022年35 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 250.500 | 115.175 | 2.175 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00003 | EVIDENCE_C | 292.000 | 120.132 | 2.431 | SCHEME_B | 2.431 | 430.162 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00004 | EVIDENCE_C | 240.000 | 103.913 | 2.310 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00005 | EVIDENCE_C | 263.000 | 124.718 | 2.109 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00007 | EVIDENCE_C | 56.000 | 11.017 | 5.083 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00008 | EVIDENCE_C | 185.600 | 107.396 | 1.728 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00009 | EVIDENCE_C | 258.300 | 87.770 | 2.943 | SCHEME_B | 2.943 | 0.000 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00010 | EVIDENCE_C | 234.500 | 117.617 | 1.994 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2023年110 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | 2.891 | 3.058 | 3.082 | 2.891 | 2.318 | — | — | 3.580 |
| 当前推荐方案代码 | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 1365.000 | 966.500 | 1994.000 | 2151.000 | 3575.000 | 1690.500 | 1907.000 | 2033.500 |
| 干预前正向同步峰值 P_plus_base（MW） | 489.475 | 316.006 | 647.049 | 761.232 | 1542.217 | 660.561 | 746.012 | 609.974 |
| 现状模型容载比 R0 | 2.789 | 3.058 | 3.082 | 2.826 | 2.318 | 2.559 | 2.556 | 3.334 |
| 官方历史参考容载比（仅作参考） | 2.790 | 3.060 | 3.080 | 2.830 | 2.320 | 2.560 | 2.560 | 3.330 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | feasible / EAC=224.091 | feasible / EAC=639.609 | feasible / EAC=556.284 | feasible / EAC=1687.982 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B联合：状态 / EAC（万元/年） | feasible / EAC=121.741 | feasible / EAC=639.609 | feasible / EAC=556.284 | feasible / EAC=712.934 | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=1674.840 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | feasible / EAC=224.091 | feasible / EAC=639.609 | feasible / EAC=556.284 | feasible / EAC=1687.982 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | feasible / EAC=121.741 | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | feasible / EAC=224.091 | feasible / EAC=639.609 | feasible / EAC=556.284 | feasible / EAC=1687.982 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2023年110 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 1365.000 | 489.475 | 2.789 | SCHEME_B | 2.891 | 121.741 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00003 | EVIDENCE_C | 966.500 | 316.006 | 3.058 | SCHEME_B | 3.058 | 639.609 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00004 | EVIDENCE_C | 1994.000 | 647.049 | 3.082 | SCHEME_B | 3.082 | 556.284 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00005 | EVIDENCE_C | 2151.000 | 761.232 | 2.826 | SCHEME_B | 2.891 | 712.934 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00007 | EVIDENCE_C | 3575.000 | 1542.217 | 2.318 | SCHEME_B | 2.318 | 0.000 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00008 | EVIDENCE_C | 1690.500 | 660.561 | 2.559 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00009 | EVIDENCE_C | 1907.000 | 746.012 | 2.556 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00010 | EVIDENCE_C | 2033.500 | 609.974 | 3.334 | SCHEME_B | 3.580 | 1674.840 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2023年35 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | — | 3.147 | — | — | — | — | 2.999 | 3.513 |
| 当前推荐方案代码 | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 276.500 | 302.000 | 250.000 | 263.000 | 36.000 | 190.600 | 258.300 | 224.000 |
| 干预前正向同步峰值 P_plus_base（MW） | 93.591 | 95.964 | 92.059 | 86.700 | 14.050 | 58.021 | 86.119 | 63.770 |
| 现状模型容载比 R0 | 2.954 | 3.147 | 2.716 | 3.033 | 2.562 | 3.285 | 2.999 | 3.513 |
| 官方历史参考容载比（仅作参考） | 2.950 | 3.150 | 2.720 | 3.030 | 2.560 | 3.290 | 3.000 | 3.510 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=171.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=888.477 |
| 方案B联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=171.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=888.477 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=171.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=888.477 |
| 方案B仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=171.162 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=888.477 |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2023年35 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 276.500 | 93.591 | 2.954 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00003 | EVIDENCE_C | 302.000 | 95.964 | 3.147 | SCHEME_B | 3.147 | 171.162 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00004 | EVIDENCE_C | 250.000 | 92.059 | 2.716 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00005 | EVIDENCE_C | 263.000 | 86.700 | 3.033 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00007 | EVIDENCE_C | 36.000 | 14.050 | 2.562 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00008 | EVIDENCE_C | 190.600 | 58.021 | 3.285 | NOT_IDENTIFIABLE | — | — | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00009 | EVIDENCE_C | 258.300 | 86.119 | 2.999 | SCHEME_B | 2.999 | 0.000 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |
| QX-00010 | EVIDENCE_C | 224.000 | 63.770 | 3.513 | SCHEME_B | 3.513 | 888.477 | diagnostic replay: 8760 sample/mapping exists but same-year asset scope, PV and candidate cost closure is unresolved |

### 2024年110 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | 2.735 | 3.319 | 3.148 | 2.573 | 2.536 | — | — | 3.267 |
| 当前推荐方案代码 | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 1365.000 | 966.500 | 1994.000 | 2169.500 | 3675.000 | 1709.000 | 1907.000 | 2063.500 |
| 干预前正向同步峰值 P_plus_base（MW） | 517.378 | 291.210 | 633.322 | 862.662 | 1449.402 | 689.656 | 738.348 | 677.527 |
| 现状模型容载比 R0 | 2.638 | 3.319 | 3.148 | 2.515 | 2.536 | 2.478 | 2.583 | 3.046 |
| 官方历史参考容载比（仅作参考） | 2.640 | 3.320 | 3.150 | 2.510 | 2.540 | 2.480 | 2.580 | 3.050 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | feasible / EAC=322.061 | feasible / EAC=377.233 | feasible / EAC=423.407 | feasible / EAC=2986.331 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B联合：状态 / EAC（万元/年） | feasible / EAC=121.741 | feasible / EAC=377.233 | feasible / EAC=423.407 | feasible / EAC=1532.703 | feasible / EAC=0.000 | infeasible | infeasible | feasible / EAC=2391.020 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | feasible / EAC=322.061 | feasible / EAC=377.233 | feasible / EAC=423.407 | feasible / EAC=2986.331 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | feasible / EAC=121.741 | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | feasible / EAC=322.061 | feasible / EAC=377.233 | feasible / EAC=423.407 | feasible / EAC=2986.331 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |

### 2024年110 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 1365.000 | 517.378 | 2.638 | SCHEME_B | 2.735 | 121.741 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00003 | EVIDENCE_C | 966.500 | 291.210 | 3.319 | SCHEME_B | 3.319 | 377.233 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00004 | EVIDENCE_C | 1994.000 | 633.322 | 3.148 | SCHEME_B | 3.148 | 423.407 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00005 | EVIDENCE_C | 2169.500 | 862.662 | 2.515 | SCHEME_B | 2.573 | 1532.703 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00007 | EVIDENCE_C | 3675.000 | 1449.402 | 2.536 | SCHEME_B | 2.536 | 0.000 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00008 | EVIDENCE_C | 1709.000 | 689.656 | 2.478 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00009 | EVIDENCE_C | 1907.000 | 738.348 | 2.583 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00010 | EVIDENCE_C | 2063.500 | 677.527 | 3.046 | SCHEME_B | 3.267 | 2391.020 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |

### 2024年35 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | — | 2.705 | — | — | — | — | 2.954 | 2.678 |
| 当前推荐方案代码 | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 276.500 | 302.000 | 250.000 | 263.000 | 36.000 | 190.600 | 270.300 | 224.000 |
| 干预前正向同步峰值 P_plus_base（MW） | 112.361 | 111.635 | 99.859 | 128.362 | 13.058 | 81.638 | 91.511 | 83.629 |
| 现状模型容载比 R0 | 2.461 | 2.705 | 2.504 | 2.049 | 2.757 | 2.335 | 2.954 | 2.678 |
| 官方历史参考容载比（仅作参考） | 2.460 | 2.710 | 2.500 | 2.050 | 2.760 | 2.330 | 2.950 | 2.680 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=308.551 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=14.644 | feasible / EAC=2512.264 |
| 方案B联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=308.551 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=14.644 | feasible / EAC=2512.264 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=308.551 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=14.644 | feasible / EAC=2512.264 |
| 方案B仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=308.551 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=14.644 | feasible / EAC=2512.264 |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |

### 2024年35 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 276.500 | 112.361 | 2.461 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00003 | EVIDENCE_C | 302.000 | 111.635 | 2.705 | SCHEME_B | 2.705 | 308.551 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00004 | EVIDENCE_C | 250.000 | 99.859 | 2.504 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00005 | EVIDENCE_C | 263.000 | 128.362 | 2.049 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00007 | EVIDENCE_C | 36.000 | 13.058 | 2.757 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00008 | EVIDENCE_C | 190.600 | 81.638 | 2.335 | NOT_IDENTIFIABLE | — | — | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00009 | EVIDENCE_C | 270.300 | 91.511 | 2.954 | SCHEME_B | 2.954 | 14.644 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |
| QX-00010 | EVIDENCE_C | 224.000 | 83.629 | 2.678 | SCHEME_B | 2.678 | 2512.264 | diagnostic replay: cross-year hourly sheet and 2024 anomaly review required; 2025 asset/cost scope reused as marked |

### 2025年110 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | 2.709 | 3.088 | 3.301 | 2.289 | 2.421 | — | — | — |
| 当前推荐方案代码 | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE |
| 同电压公用变容量 S0（MVA） | 1425.000 | 966.500 | 2094.000 | 2139.500 | 3701.000 | 1839.000 | 1877.000 | 1979.500 |
| 干预前正向同步峰值 P_plus_base（MW） | 544.550 | 313.030 | 634.280 | 956.450 | 1528.820 | 759.560 | 813.380 | 734.910 |
| 现状模型容载比 R0 | 2.617 | 3.088 | 3.301 | 2.237 | 2.421 | 2.421 | 2.308 | 2.694 |
| 官方历史参考容载比（仅作参考） | 2.620 | 3.090 | 3.300 | 2.240 | 2.420 | 2.420 | 2.310 | 2.690 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | feasible / EAC=483.091 | feasible / EAC=604.702 | feasible / EAC=433.539 | feasible / EAC=4417.557 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B联合：状态 / EAC（万元/年） | feasible / EAC=189.314 | feasible / EAC=604.702 | feasible / EAC=433.539 | feasible / EAC=2549.545 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | feasible / EAC=483.091 | feasible / EAC=604.702 | feasible / EAC=433.539 | feasible / EAC=4417.557 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅扩容：状态 / EAC（万元/年） | feasible / EAC=697.476 | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | feasible / EAC=483.091 | feasible / EAC=604.702 | feasible / EAC=433.539 | feasible / EAC=4417.557 | feasible / EAC=0.000 | infeasible | infeasible | infeasible |
| 证据等级 | EVIDENCE_B | EVIDENCE_B | EVIDENCE_B | EVIDENCE_C | EVIDENCE_B | EVIDENCE_B | EVIDENCE_B | EVIDENCE_B |
| 质量备注 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | 2025 transformer-hour map is not source-owner approved; reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |

### 2025年110 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_B | 1425.000 | 544.550 | 2.617 | SCHEME_B | 2.709 | 189.314 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00003 | EVIDENCE_B | 966.500 | 313.030 | 3.088 | SCHEME_B | 3.088 | 604.702 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00004 | EVIDENCE_B | 2094.000 | 634.280 | 3.301 | SCHEME_B | 3.301 | 433.539 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00005 | EVIDENCE_C | 2139.500 | 956.450 | 2.237 | SCHEME_B | 2.289 | 2549.545 | 2025 transformer-hour map is not source-owner approved; reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00007 | EVIDENCE_B | 3701.000 | 1528.820 | 2.421 | SCHEME_B | 2.421 | 0.000 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00008 | EVIDENCE_B | 1839.000 | 759.560 | 2.421 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00009 | EVIDENCE_B | 1877.000 | 813.380 | 2.308 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00010 | EVIDENCE_B | 1979.500 | 734.910 | 2.694 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |

### 2025年35 kV甲方转置式推荐主表

| 指标 | QX-00001 | QX-00003 | QX-00004 | QX-00005 | QX-00007 | QX-00008 | QX-00009 | QX-00010 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 当前推荐容载比 R_rec（成本最小可行方案） | — | 2.420 | — | — | — | — | 3.082 | 2.909 |
| 当前推荐方案代码 | NOT_IDENTIFIABLE | SCHEME_B | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | NOT_IDENTIFIABLE | SCHEME_B | SCHEME_B |
| 同电压公用变容量 S0（MVA） | 276.500 | 302.000 | 250.000 | 275.000 | 36.000 | 164.300 | 274.300 | 232.000 |
| 干预前正向同步峰值 P_plus_base（MW） | 119.490 | 124.780 | 106.610 | 147.650 | 14.680 | 82.310 | 89.000 | 79.750 |
| 现状模型容载比 R0 | 2.314 | 2.420 | 2.345 | 1.863 | 2.452 | 1.996 | 3.082 | 2.909 |
| 官方历史参考容载比（仅作参考） | 2.310 | 2.420 | 2.340 | 1.860 | 2.450 | 2.000 | 3.080 | 2.910 |
| C0状态（现状不采取措施） | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | noncompliant / EAC=0.000 | compliant / EAC=0.000 | noncompliant / EAC=0.000 |
| 方案A联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=506.732 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=2141.786 |
| 方案B联合：状态 / EAC（万元/年） | infeasible | feasible / EAC=506.732 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=2141.786 |
| 方案A仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案A仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=506.732 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=2141.786 |
| 方案B仅扩容：状态 / EAC（万元/年） | infeasible | infeasible | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | infeasible |
| 方案B仅配储：状态 / EAC（万元/年） | infeasible | feasible / EAC=506.732 | infeasible | infeasible | infeasible | infeasible | feasible / EAC=0.000 | feasible / EAC=2141.786 |
| 证据等级 | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C | EVIDENCE_C |
| 质量备注 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | 2025 transformer-hour map is not source-owner approved; reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |

### 2025年35 kV精确查值附表（精确查值表）

| 脱敏片区 | 证据等级 | S0（MVA） | P_plus_base（MW） | R0 | 当前推荐方案 | R_rec | 推荐EAC（万元/年） | 质量备注 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 276.500 | 119.490 | 2.314 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00003 | EVIDENCE_C | 302.000 | 124.780 | 2.420 | SCHEME_B | 2.420 | 506.732 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00004 | EVIDENCE_C | 250.000 | 106.610 | 2.345 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00005 | EVIDENCE_C | 275.000 | 147.650 | 1.863 | NOT_IDENTIFIABLE | — | — | 2025 transformer-hour map is not source-owner approved; reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00007 | EVIDENCE_C | 36.000 | 14.680 | 2.452 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00008 | EVIDENCE_C | 164.300 | 82.310 | 1.996 | NOT_IDENTIFIABLE | — | — | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00009 | EVIDENCE_C | 274.300 | 89.000 | 3.082 | SCHEME_B | 3.082 | 0.000 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |
| QX-00010 | EVIDENCE_C | 232.000 | 79.750 | 2.909 | SCHEME_B | 2.909 | 2141.786 | reverse static extrema are bounds, not synchronous county peaks; 2026 PV is context only |

### 110 kV最终推荐区间矩阵

| 脱敏片区 | 证据等级 | 五年历史参考下限 R | 五年历史参考上限 R | 五年模型口径下限 R | 五年模型口径上限 R | 2025当前推荐方案 | 2025当前推荐 R_rec | 最终推荐区间下限 | 最终推荐区间上限 | 解释 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_B | 2.570 | 2.890 | 2.565 | 2.887 | SCHEME_B | 2.709 | 2.570 | 2.890 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00003 | EVIDENCE_B | 2.630 | 3.320 | 2.633 | 3.319 | SCHEME_B | 3.088 | 2.630 | 3.320 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00004 | EVIDENCE_B | 2.910 | 3.300 | 2.912 | 3.301 | SCHEME_B | 3.301 | 2.910 | 3.301 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00005 | EVIDENCE_C | 2.240 | 2.830 | 2.237 | 2.826 | SCHEME_B | 2.289 | 2.240 | 2.830 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00007 | EVIDENCE_B | 2.150 | 2.540 | 2.148 | 2.536 | SCHEME_B | 2.421 | 2.150 | 2.540 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00008 | EVIDENCE_C | 2.250 | 2.560 | 2.252 | 2.559 | NOT_IDENTIFIABLE | — | 2.250 | 2.560 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00009 | EVIDENCE_C | 2.310 | 2.580 | 2.308 | 2.583 | NOT_IDENTIFIABLE | — | 2.310 | 2.580 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00010 | EVIDENCE_C | 2.690 | 3.400 | 2.694 | 3.399 | NOT_IDENTIFIABLE | — | 2.690 | 3.400 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |

### 35 kV最终推荐区间矩阵

| 脱敏片区 | 证据等级 | 五年历史参考下限 R | 五年历史参考上限 R | 五年模型口径下限 R | 五年模型口径上限 R | 2025当前推荐方案 | 2025当前推荐 R_rec | 最终推荐区间下限 | 最终推荐区间上限 | 解释 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| QX-00001 | EVIDENCE_C | 2.170 | 2.950 | 2.175 | 2.954 | NOT_IDENTIFIABLE | — | 2.170 | 2.950 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00003 | EVIDENCE_C | 2.300 | 3.150 | 2.303 | 3.147 | SCHEME_B | 2.420 | 2.300 | 3.150 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00004 | EVIDENCE_C | 1.810 | 2.720 | 1.811 | 2.716 | NOT_IDENTIFIABLE | — | 1.810 | 2.720 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00005 | EVIDENCE_C | 1.860 | 3.030 | 1.863 | 3.034 | NOT_IDENTIFIABLE | — | 1.860 | 3.030 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00007 | EVIDENCE_C | 1.730 | 5.080 | 1.727 | 5.083 | NOT_IDENTIFIABLE | — | 1.730 | 5.080 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00008 | EVIDENCE_C | 1.730 | 3.290 | 1.728 | 3.285 | NOT_IDENTIFIABLE | — | 1.730 | 3.290 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00009 | EVIDENCE_C | 2.430 | 3.080 | 2.432 | 3.082 | SCHEME_B | 3.082 | 2.430 | 3.082 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |
| QX-00010 | EVIDENCE_C | 1.990 | 3.510 | 1.994 | 3.513 | SCHEME_B | 2.909 | 1.990 | 3.510 | 五年官方静态容载比参考区间与2025当前成本最小可行方案的包络，不是未来阈值或历史回测 |