## 年度参数及推荐
研究单元编号 | 电压等级_kV | 年份 | 站数 | 源荷出力代理比 | 光伏代理出力和_MW | 毛负荷代理和_MW | 源荷比计算边界 | 净峰年均增长率_CAGR | 净峰同比增长率 | 正向参考净峰_MW | 反向最大站峰_MW | 反向站峰和上包络_MW | 反向极值计算边界 | 正向最长连续D95_h | 反向最长连续D95_h | 持续时间来源 | 主变价格系数 | 线路价格系数 | 储能价格系数 | 主变相对储能成本比系数 | 线路相对储能成本比系数 | 2021起点容量_MVA | 停运恢复负荷比例 | 刚性累计增配预算比例 | 转供候选范围 | 刚性容载比 | 弹性容载比 | 推荐方案 | 推荐容载比 | 推荐容量_MVA | 在役储能柜数 | 既有线路转供_MW | 新线路转供_MW | 该年新增措施全寿命现值_万元 | 刚性全路径现值_万元 | 弹性全路径现值_万元 | 推荐依据 | 适用状态
QX-00005 | 35 | 2022 | 8 | 0.55028 | 19.6466 | 35.703 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 54.43% | 54.43% | 124.7177 | 1.0207 | 1.0207 | station_extrema_not_synchronous_regional_reverse_peak | 3 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 245 | 60% | 30% | no_station_tie_candidates | 1.9805 | 2.0125 | 弹性 | 2.0125 | 251 | 0 | 0 | 0 | 259.7325 | 3737.4794 | 1517.7393 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 35 | 2023 | 8 | 1.9218 | 47.6983 | 24.8197 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 3.612% | -30.48% | 86.7 | 6.8031 | 23.5029 | station_extrema_not_synchronous_regional_reverse_peak | 3 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 245 | 60% | 30% | no_station_tie_candidates | 1.9839 | 2.895 | 弹性 | 2.895 | 251 | 0 | 0 | 0 | 0 | 3737.4794 | 1517.7393 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 35 | 2024 | 8 | 3.1755 | 116.6882 | 36.7462 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 16.7% | 48.05% | 128.3615 | 18.8683 | 80.026 | station_extrema_not_synchronous_regional_reverse_peak | 3 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 245 | 60% | 30% | no_station_tie_candidates | 1.8386 | 1.9554 | 弹性 | 1.9554 | 251 | 0 | 0 | 0 | 0 | 3737.4794 | 1517.7393 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 35 | 2025 | 8 | 4.0657 | 171.755 | 42.245 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 16.28% | 15.03% | 147.65 | 26.87 | 134.63 | station_extrema_not_synchronous_regional_reverse_peak | 3 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 245 | 60% | 30% | no_station_tie_candidates | 1.5984 | 1.8151 | 弹性 | 1.8151 | 268 | 12 | 0 | 0 | 1258.0068 | 3737.4794 | 1517.7393 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 110 | 2022 | 20 | 0.30981 | 77.3917 | 249.8003 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 12.74% | 12.74% | 825.0042 | 0.67947 | 1.0725 | station_extrema_not_synchronous_regional_reverse_peak | 4 | 3 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2027 | 60% | 3% | T01_and_designed_new_line | 2 | 2.5267 | 弹性 | 2.5267 | 2084.5 | 0 | 3.8786 | 0 | 2737.3211 | 5245.6612 | 4410.4406 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 110 | 2023 | 20 | 0.85761 | 197.6722 | 230.4909 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 1.993% | -7.73% | 761.2318 | 11.4463 | 37.2538 | station_extrema_not_synchronous_regional_reverse_peak | 4 | 3 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2027 | 60% | 3% | T01_and_designed_new_line | 1.9994 | 2.7383 | 弹性 | 2.7383 | 2084.5 | 0 | 0 | 0 | 0 | 5245.6612 | 4410.4406 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 110 | 2024 | 20 | 1.939 | 506.4777 | 261.2024 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 5.638% | 13.32% | 862.6615 | 33.5286 | 268.9419 | station_extrema_not_synchronous_regional_reverse_peak | 4 | 3 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2027 | 60% | 3% | T01_and_designed_new_line | 1.7643 | 2.4164 | 弹性 | 2.4164 | 2084.5 | 0 | 4.0556 | 0 | 0 | 5245.6612 | 4410.4406 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00005 | 110 | 2025 | 20 | 2.7049 | 779.41 | 288.15 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 6.923% | 10.87% | 956.45 | 56.92 | 509.59 | station_extrema_not_synchronous_regional_reverse_peak | 4 | 3 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2027 | 60% | 3% | T01_and_designed_new_line | 1.6033 | 2.1914 | 弹性 | 2.1914 | 2096 | 35 | 4.4965 | 7.4911 | 1673.1195 | 5245.6612 | 4410.4406 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00007 | 110 | 2022 | 29 | 0.20056 | 82.1471 | 409.5962 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | -1.2% | -1.2% | 1224.8396 | 0.53282 | 0.53282 | station_extrema_not_synchronous_regional_reverse_peak | 5 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2948 | 45% | 1% | no_station_tie_candidates | 1.9921 | 2.4256 | 弹性 | 2.4256 | 2971 | 0 | 0 | 0 | 1094.9284 | 3211.1507 | 1912.2935 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00007 | 110 | 2023 | 29 | 0.27629 | 121.8476 | 441.0076 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 3.139% | 7.669% | 1318.7711 | 4.9596 | 6.253 | station_extrema_not_synchronous_regional_reverse_peak | 5 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2948 | 45% | 1% | no_station_tie_candidates | 1.8578 | 2.2604 | 弹性 | 2.2604 | 2981 | 0 | 0 | 0 | 817.3651 | 3211.1507 | 1912.2935 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00007 | 110 | 2024 | 29 | 0.43614 | 180.7636 | 414.4665 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | -0.008472% | -6.018% | 1239.4036 | 14.9962 | 22.3142 | station_extrema_not_synchronous_regional_reverse_peak | 5 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2948 | 45% | 1% | no_station_tie_candidates | 1.9768 | 2.4052 | 弹性 | 2.4052 | 2981 | 0 | 0 | 0 | 0 | 3211.1507 | 1912.2935 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region
QX-00007 | 110 | 2025 | 29 | 0.61647 | 269.5048 | 437.1767 | noncoincident_station_reverse_templates_output_over_gross_proxy_not_installed_capacity_ratio | 1.336% | 5.479% | 1307.3154 | 30.5567 | 82.3404 | station_extrema_not_synchronous_regional_reverse_peak | 5 | 2 | 2025_station_templates_held_for_2022_2025_not_observed_annual_durations | 1 | 1 | 1 | 1 | 1 | 2948 | 45% | 1% | no_station_tie_candidates | 1.8741 | 2.2802 | 弹性 | 2.2802 | 2981 | 0 | 0 | 0 | 0 | 3211.1507 | 1912.2935 | minimum_full_path_cost_given_station_distribution_initial_assets_and_network_scope | annual_case_lookup_reference_reoptimization_required_for_new_region

## 价格敏感性年度推荐
情景 | 研究单元编号 | 电压等级_kV | 年份 | 主变价格系数 | 储能价格系数 | 线路价格系数 | 推荐方案 | 推荐容载比 | 推荐容量_MVA | 在役储能柜数 | 刚性全路径现值_万元 | 弹性全路径现值_万元 | 统计范围
基准 | QX-00005 | 110 | 2022 | 1 | 1 | 1 | 弹性 | 2.5267 | 2084.5 | 0 | 5245.6612 | 4410.4406 | pizhou_110_representative_case_not_all_regions
基准 | QX-00005 | 110 | 2023 | 1 | 1 | 1 | 弹性 | 2.7383 | 2084.5 | 0 | 5245.6612 | 4410.4406 | pizhou_110_representative_case_not_all_regions
基准 | QX-00005 | 110 | 2024 | 1 | 1 | 1 | 弹性 | 2.4164 | 2084.5 | 0 | 5245.6612 | 4410.4406 | pizhou_110_representative_case_not_all_regions
基准 | QX-00005 | 110 | 2025 | 1 | 1 | 1 | 弹性 | 2.1914 | 2096 | 35 | 5245.6612 | 4410.4406 | pizhou_110_representative_case_not_all_regions
主变价格×0.7 | QX-00005 | 110 | 2022 | 0.7 | 1 | 1 | 弹性 | 2.5267 | 2084.5 | 0 | 4355.6531 | 3260.9821 | pizhou_110_representative_case_not_all_regions
主变价格×0.7 | QX-00005 | 110 | 2023 | 0.7 | 1 | 1 | 弹性 | 2.7383 | 2084.5 | 0 | 4355.6531 | 3260.9821 | pizhou_110_representative_case_not_all_regions
主变价格×0.7 | QX-00005 | 110 | 2024 | 0.7 | 1 | 1 | 弹性 | 2.4164 | 2084.5 | 0 | 4355.6531 | 3260.9821 | pizhou_110_representative_case_not_all_regions
主变价格×0.7 | QX-00005 | 110 | 2025 | 0.7 | 1 | 1 | 弹性 | 2.2092 | 2113 | 3 | 4355.6531 | 3260.9821 | pizhou_110_representative_case_not_all_regions
储能价格×1.5 | QX-00005 | 110 | 2022 | 1 | 1.5 | 1 | 弹性 | 2.5267 | 2084.5 | 0 | 6326.8732 | 4615.7527 | pizhou_110_representative_case_not_all_regions
储能价格×1.5 | QX-00005 | 110 | 2023 | 1 | 1.5 | 1 | 弹性 | 2.7383 | 2084.5 | 0 | 6326.8732 | 4615.7527 | pizhou_110_representative_case_not_all_regions
储能价格×1.5 | QX-00005 | 110 | 2024 | 1 | 1.5 | 1 | 弹性 | 2.4164 | 2084.5 | 0 | 6326.8732 | 4615.7527 | pizhou_110_representative_case_not_all_regions
储能价格×1.5 | QX-00005 | 110 | 2025 | 1 | 1.5 | 1 | 弹性 | 2.2092 | 2113 | 3 | 6326.8732 | 4615.7527 | pizhou_110_representative_case_not_all_regions
线路价格×1.5 | QX-00005 | 110 | 2022 | 1 | 1 | 1.5 | 弹性 | 2.5267 | 2084.5 | 0 | 5303.9329 | 4468.7123 | pizhou_110_representative_case_not_all_regions
线路价格×1.5 | QX-00005 | 110 | 2023 | 1 | 1 | 1.5 | 弹性 | 2.7383 | 2084.5 | 0 | 5303.9329 | 4468.7123 | pizhou_110_representative_case_not_all_regions
线路价格×1.5 | QX-00005 | 110 | 2024 | 1 | 1 | 1.5 | 弹性 | 2.4164 | 2084.5 | 0 | 5303.9329 | 4468.7123 | pizhou_110_representative_case_not_all_regions
线路价格×1.5 | QX-00005 | 110 | 2025 | 1 | 1 | 1.5 | 弹性 | 2.1914 | 2096 | 35 | 5303.9329 | 4468.7123 | pizhou_110_representative_case_not_all_regions

## 价格敏感性成本
情景 | 方案 | 主变价格系数 | 储能价格系数 | 线路价格系数 | 求解状态 | 全路径成本现值_万元 | 补充说明
基准 | 刚性 | 1 | 1 | 1 | optimal | 5245.6612
基准 | 弹性 | 1 | 1 | 1 | optimal | 4410.4406
主变价格×0.7 | 刚性 | 0.7 | 1 | 1 | optimal | 4355.6531
主变价格×0.7 | 弹性 | 0.7 | 1 | 1 | optimal | 3260.9821
储能价格×1.5 | 刚性 | 1 | 1.5 | 1 | optimal | 6326.8732
储能价格×1.5 | 弹性 | 1 | 1.5 | 1 | optimal | 4615.7527
线路价格×1.5 | 刚性 | 1 | 1 | 1.5 | optimal | 5303.9329
线路价格×1.5 | 弹性 | 1 | 1 | 1.5 | optimal | 4468.7123

## 价格敏感性刚弹明细
情景 | 方案 | 年份 | 主变价格系数 | 储能价格系数 | 线路价格系数 | transformer_storage_relative_cost_multiplier | line_storage_relative_cost_multiplier | 容量_MVA | 容载比 | 在役储能柜数 | 新线路在役 | 该年新增措施全寿命现值_万元 | 全路径成本现值_万元
基准 | 刚性 | 2022 | 1 | 1 | 1 | 1 | 1 | 1650 | 2 | 0 | 0 | 2511.3834 | 5245.6612
基准 | 刚性 | 2023 | 1 | 1 | 1 | 1 | 1 | 1522 | 1.9994 | 0 | 0 | 0 | 5245.6612
基准 | 刚性 | 2024 | 1 | 1 | 1 | 1 | 1 | 1522 | 1.7643 | 0 | 0 | 0 | 5245.6612
基准 | 刚性 | 2025 | 1 | 1 | 1 | 1 | 1 | 1533.5 | 1.6033 | 69 | 1 | 2734.2778 | 5245.6612
基准 | 弹性 | 2022 | 1 | 1 | 1 | 1 | 1 | 2084.5 | 2.5267 | 0 | 0 | 2737.3211 | 4410.4406
基准 | 弹性 | 2023 | 1 | 1 | 1 | 1 | 1 | 2084.5 | 2.7383 | 0 | 0 | 0 | 4410.4406
基准 | 弹性 | 2024 | 1 | 1 | 1 | 1 | 1 | 2084.5 | 2.4164 | 0 | 0 | 0 | 4410.4406
基准 | 弹性 | 2025 | 1 | 1 | 1 | 1 | 1 | 2096 | 2.1914 | 35 | 1 | 1673.1195 | 4410.4406
主变价格×0.7 | 刚性 | 2022 | 0.7 | 1 | 1 | 0.7 | 1 | 1650 | 2 | 0 | 0 | 1757.9684 | 4355.6531
主变价格×0.7 | 刚性 | 2023 | 0.7 | 1 | 1 | 0.7 | 1 | 1522 | 1.9994 | 0 | 0 | 0 | 4355.6531
主变价格×0.7 | 刚性 | 2024 | 0.7 | 1 | 1 | 0.7 | 1 | 1522 | 1.7643 | 0 | 0 | 0 | 4355.6531
主变价格×0.7 | 刚性 | 2025 | 0.7 | 1 | 1 | 0.7 | 1 | 1533.5 | 1.6033 | 69 | 1 | 2597.6847 | 4355.6531
主变价格×0.7 | 弹性 | 2022 | 0.7 | 1 | 1 | 0.7 | 1 | 2084.5 | 2.5267 | 0 | 0 | 1916.1247 | 3260.9821
主变价格×0.7 | 弹性 | 2023 | 0.7 | 1 | 1 | 0.7 | 1 | 2084.5 | 2.7383 | 0 | 0 | 0 | 3260.9821
主变价格×0.7 | 弹性 | 2024 | 0.7 | 1 | 1 | 0.7 | 1 | 2084.5 | 2.4164 | 0 | 0 | 0 | 3260.9821
主变价格×0.7 | 弹性 | 2025 | 0.7 | 1 | 1 | 0.7 | 1 | 2113 | 2.2092 | 3 | 1 | 1344.8574 | 3260.9821
储能价格×1.5 | 刚性 | 2022 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 1650 | 2 | 0 | 0 | 2511.3834 | 6326.8732
储能价格×1.5 | 刚性 | 2023 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 1522 | 1.9994 | 0 | 0 | 0 | 6326.8732
储能价格×1.5 | 刚性 | 2024 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 1522 | 1.7643 | 0 | 0 | 0 | 6326.8732
储能价格×1.5 | 刚性 | 2025 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 1533.5 | 1.6033 | 69 | 1 | 3815.4898 | 6326.8732
储能价格×1.5 | 弹性 | 2022 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 2084.5 | 2.5267 | 0 | 0 | 2737.3211 | 4615.7527
储能价格×1.5 | 弹性 | 2023 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 2084.5 | 2.7383 | 0 | 0 | 0 | 4615.7527
储能价格×1.5 | 弹性 | 2024 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 2084.5 | 2.4164 | 0 | 0 | 0 | 4615.7527
储能价格×1.5 | 弹性 | 2025 | 1 | 1.5 | 1 | 0.66667 | 0.66667 | 2113 | 2.2092 | 3 | 1 | 1878.4316 | 4615.7527
线路价格×1.5 | 刚性 | 2022 | 1 | 1 | 1.5 | 1 | 1.5 | 1650 | 2 | 0 | 0 | 2511.3834 | 5303.9329
线路价格×1.5 | 刚性 | 2023 | 1 | 1 | 1.5 | 1 | 1.5 | 1522 | 1.9994 | 0 | 0 | 0 | 5303.9329
线路价格×1.5 | 刚性 | 2024 | 1 | 1 | 1.5 | 1 | 1.5 | 1522 | 1.7643 | 0 | 0 | 0 | 5303.9329
线路价格×1.5 | 刚性 | 2025 | 1 | 1 | 1.5 | 1 | 1.5 | 1533.5 | 1.6033 | 69 | 1 | 2792.5495 | 5303.9329
线路价格×1.5 | 弹性 | 2022 | 1 | 1 | 1.5 | 1 | 1.5 | 2084.5 | 2.5267 | 0 | 0 | 2737.3211 | 4468.7123
线路价格×1.5 | 弹性 | 2023 | 1 | 1 | 1.5 | 1 | 1.5 | 2084.5 | 2.7383 | 0 | 0 | 0 | 4468.7123
线路价格×1.5 | 弹性 | 2024 | 1 | 1 | 1.5 | 1 | 1.5 | 2084.5 | 2.4164 | 0 | 0 | 0 | 4468.7123
线路价格×1.5 | 弹性 | 2025 | 1 | 1 | 1.5 | 1 | 1.5 | 2096 | 2.1914 | 35 | 1 | 1731.3912 | 4468.7123

## 指标相关性
统计范围 | 样本数 | 指标A | 指标B | Pearson相关系数 | Spearman相关系数 | 高相关标记_绝对值0.8 | 解释边界
all_12_rows | 12 | 源荷出力代理比 | 净峰年均增长率_CAGR | 0.091413 | 0.53846 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 源荷出力代理比 | 正向参考净峰_MW | -0.61012 | -0.51049 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 源荷出力代理比 | 反向最大站峰_MW | 0.58288 | 0.75524 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 源荷出力代理比 | 正向最长连续D95_h | -0.66436 | -0.68001 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 源荷出力代理比 | 反向最长连续D95_h | 0.017807 | 0.15363 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 净峰年均增长率_CAGR | 正向参考净峰_MW | -0.61586 | -0.66434 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 净峰年均增长率_CAGR | 反向最大站峰_MW | -0.20798 | 0.11888 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 净峰年均增长率_CAGR | 正向最长连续D95_h | -0.61482 | -0.82784 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 净峰年均增长率_CAGR | 反向最长连续D95_h | -0.16058 | 0.10242 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 正向参考净峰_MW | 反向最大站峰_MW | 0.11035 | 0.11189 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 正向参考净峰_MW | 正向最长连续D95_h | 0.98307 | 0.9461 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 正向参考净峰_MW | 反向最长连续D95_h | 0.15203 | 0 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 反向最大站峰_MW | 正向最长连续D95_h | -0.015663 | -0.088697 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 反向最大站峰_MW | 反向最长连续D95_h | 0.36126 | 0.25605 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
all_12_rows | 12 | 正向最长连续D95_h | 反向最长连续D95_h | 0 | 0 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 源荷出力代理比 | 净峰年均增长率_CAGR | -0.64365 | -0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 源荷出力代理比 | 正向参考净峰_MW | 0.50845 | 0.8 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 源荷出力代理比 | 反向最大站峰_MW | 0.98497 | 1 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 源荷出力代理比 | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 源荷出力代理比 | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 净峰年均增长率_CAGR | 正向参考净峰_MW | 0.33145 | 0.2 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 净峰年均增长率_CAGR | 反向最大站峰_MW | -0.50225 | -0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 净峰年均增长率_CAGR | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 净峰年均增长率_CAGR | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 正向参考净峰_MW | 反向最大站峰_MW | 0.64932 | 0.8 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_35 | 4 | 正向参考净峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 正向参考净峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 反向最大站峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 反向最大站峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_35 | 4 | 正向最长连续D95_h | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 源荷出力代理比 | 净峰年均增长率_CAGR | -0.3016 | -0.2 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 源荷出力代理比 | 正向参考净峰_MW | 0.83916 | 0.8 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 源荷出力代理比 | 反向最大站峰_MW | 0.99489 | 1 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 源荷出力代理比 | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 源荷出力代理比 | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 净峰年均增长率_CAGR | 正向参考净峰_MW | 0.25295 | 0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 净峰年均增长率_CAGR | 反向最大站峰_MW | -0.25571 | -0.2 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 净峰年均增长率_CAGR | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 净峰年均增长率_CAGR | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 正向参考净峰_MW | 反向最大站峰_MW | 0.8702 | 0.8 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00005_110 | 4 | 正向参考净峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 正向参考净峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 反向最大站峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 反向最大站峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00005_110 | 4 | 正向最长连续D95_h | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 源荷出力代理比 | 净峰年均增长率_CAGR | 0.19173 | 0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 源荷出力代理比 | 正向参考净峰_MW | 0.38684 | 0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 源荷出力代理比 | 反向最大站峰_MW | 0.99592 | 1 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 源荷出力代理比 | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 源荷出力代理比 | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 净峰年均增长率_CAGR | 正向参考净峰_MW | 0.94127 | 1 | TRUE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 净峰年均增长率_CAGR | 反向最大站峰_MW | 0.18735 | 0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 净峰年均增长率_CAGR | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 净峰年均增长率_CAGR | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 正向参考净峰_MW | 反向最大站峰_MW | 0.40584 | 0.4 | FALSE | descriptive_small_nonindependent_sample_not_causal_or_generalizable
QX-00007_110 | 4 | 正向参考净峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 正向参考净峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 反向最大站峰_MW | 正向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 反向最大站峰_MW | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable
QX-00007_110 | 4 | 正向最长连续D95_h | 反向最长连续D95_h |  |  | FALSE | constant_indicator_not_identifiable

## 案例参数范围
研究单元编号 | 电压等级_kV | 指标 | 最小值 | 最大值 | 统计范围
QX-00005 | 35 | 源荷出力代理比 | 0.55028 | 4.0657 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 35 | 净峰年均增长率_CAGR | 0.036123 | 0.5443 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 35 | 正向参考净峰_MW | 86.7 | 147.65 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 35 | 反向最大站峰_MW | 1.0207 | 26.87 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 35 | 正向最长连续D95_h | 3 | 3 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 35 | 反向最长连续D95_h | 2 | 2 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 源荷出力代理比 | 0.30981 | 2.7049 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 净峰年均增长率_CAGR | 0.019932 | 0.12741 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 正向参考净峰_MW | 761.2318 | 956.45 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 反向最大站峰_MW | 0.67947 | 56.92 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 正向最长连续D95_h | 4 | 4 | observed_model_case_envelope_not_joint_feasibility_box
QX-00005 | 110 | 反向最长连续D95_h | 3 | 3 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 源荷出力代理比 | 0.20056 | 0.61647 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 净峰年均增长率_CAGR | -0.012002 | 0.031391 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 正向参考净峰_MW | 1224.8396 | 1318.7711 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 反向最大站峰_MW | 0.53282 | 30.5567 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 正向最长连续D95_h | 5 | 5 | observed_model_case_envelope_not_joint_feasibility_box
QX-00007 | 110 | 反向最长连续D95_h | 2 | 2 | observed_model_case_envelope_not_joint_feasibility_box

## 指标口径及来源
指标 | 定义 | 来源 | 边界
源荷比 | 光伏出力代理和/毛负荷代理和；站级反向模板时刻可能不同 | annual_reverse_station_proxy_2021_2025.csv, night_central | 不是实测同步源荷比或装机容量比
净峰平均增长率 | (该年正向参考净峰/2021参考净峰)^(1/(年-2021))-1；另列同比 | annual_forward_layer_scenes_2021_2025.csv | 净峰CAGR，不是全年平均净负荷增长率
净负荷极值 | 正向参考净峰；反向最大站峰及站峰和上包络 | 甲方年度降压负荷；transformer_only_path_station_2021_2025.csv | 市区为29站代理；反向不是同步区域峰
95%峰值持续时间 | 站级≥95%峰值的最长连续时长D95，汇总取最大；另提供各站原始模板 | static_storage_need_screen_2025.csv | 2025模板沿用至各年，不是2022—2024实测
成本比系数 | 各技术价格/各自基准价格；相对比为kT/kS、kL/kS | 本地工程案例与储能价格表 | 单位不同的原始单价不可直接相除；独立变动一项后全路径重求
推荐容载比 | 最低全路径成本方案该年容量/该年正向参考净峰 | reserve_policy_v4完整四年路径 | 需要基期资产、站级分布、网络候选和停运比例等条件