Engineering-Prior-Guided NSGA-II for Elastic Capacity-Load Ratio Planning under High Distributed Photovoltaic Penetration

Heng Xu

School of Electrical Engineering

China University of Mining and Technology

Xuzhou, Jiangsu, China

ts24230188p31@cumt.edu.cn

Abstract—High-penetration distributed PV challenges fixed capacity-load ratio planning in county 110 kV grids by introducing reverse power and changing N-1 supply risk. This paper formulates an elastic per-station planning model that couples capacity-load ratio, storage power, reverse-power constraints, and supply risk. Engineering-Prior-Guided NSGA-II (EPG-NSGA-II) combines feasibility-aware initialization with repair projection to improve constrained search efficiency. In a synthetic county case with K=20, the selected elastic configuration reduces the annualized cost index by 13.1% relative to the uniform R=2.0 baseline under equal EENS. At K=40, EPG-NSGA-II reaches a comparable hypervolume with fewer evaluations than plain NSGA-II.

Index Terms—Distributed photovoltaics, capacity-load ratio, NSGA-II, multi-objective optimization, storage planning.

I.  INTRODUCTION

High-penetration distributed PV is making county 110 kV grids increasingly bidirectional. Midday PV output may exceed local demand, causing reverse power and changing the N-1 supply margin [3]. A uniform county-wide capacity-load ratio may over-invest at moderate-PV stations while failing to reflect reverse-power pressure at PV-dense stations [1], [2]. Existing planning often relies on rigid ratio rules, while evolutionary optimization can search the cost-risk trade-off directly [1], [2], [5], [6]. Under strong engineering constraints, random initialization and variation can generate many infeasible individuals.

This paper proposes EPG-NSGA-II to address this feasibility bottleneck. It keeps nondominated sorting unchanged and adds two engineering-prior operators: warm-start sampling within engineering bounds and repair projection after variation. The contributions are threefold: an elastic capacity-load ratio model with reverse-power and N-1 constraints, an EPG-NSGA-II strategy with warm-start sampling and repair projection, and a synthetic county case with ablation analysis.

II.  ENGINEERING-PRIOR-GUIDED NSGA-II

A.  Planning Model

The model considers a set of 110 kV substations. Each station is assigned two planning variables: a capacity-load ratio and a storage power rating for absorbing reverse power. Current peak loads are projected to the planning year with a 5% annual growth rate over a five-year horizon. The projected load of station j, denoted by Ljp, is used consistently in the capacity, reverse-power, and N-1 risk terms.

The pre-storage midday reverse injection at station j is denoted by rj0. After storage absorption, the residual reverse power is given by

|  | rj(Pj)=max{0,rj0−Pj} . | (1) |
| --- | --- | --- |

Here, Pj denotes the storage power rating assigned to station j . rj(Pj) is the residual reverse power after storage absorption. The capacity-load ratio Rj is bounded within [1.2, 3.0], and the storage power rating Pj is bounded within [0, 6] MW. The regional capacity-load ratio is constrained by the planning band in (2),

|  | 1.8≤jRjLjp/(jLjp)≤2.2 . | (2) |
| --- | --- | --- |

This ratio is total planned capacity divided by the county planning-year peak. Residual reverse power is constrained at both station and upstream levels,

|  | rj(Pj)≤βRjLjp ηjrj(Pj)≤βR220δjLjp . | (3) |
| --- | --- | --- |

where β = 0.85 is the transformer reverse-loading limit, R220 = 1.8 the upper-level capacity-load ratio, δ = 0.85 the upstream coincidence factor, and η = 1.0 the reverse coincidence factor.

The first inequality limits station-level residual reverse power, while the second limits aggregated reverse power at the upstream interface.

The optimization minimizes two conflicting objectives: annualized cost and N-1 supply risk,

|  | min (f1, f2) f1=j(cRRjLjp+cPPj+Cjloss+Cjom) f2=j​EENSj(Rj,Tj,Ljp) . | (4) |
| --- | --- | --- |

Here, f1 is the annualized cost objective and f2 is the N-1 risk objective. The parameters cR and cP are annualized unit costs, while Cjloss and Cjom denote annualized loss and O&M costs. The N-1 risk f2 is the total EENS,

|  | EENSj=s∈Ωjpshsmax{0,Ljp−Sj,s} . | (5) |
| --- | --- | --- |

In (5), Ωj is the outage-state set, ps and hs are the probability and duration of state s, and Sj,s is the available supply determined by transformer capacity and fixed tie-line support.

Storage is considered only for reverse-power absorption and is not credited as firm N-1 backup. The resulting optimization is subject to the variable bounds, the regional ratio band, and the reverse-power constraints.

B.  EPG-NSGA-II Procedure

EPG-NSGA-II retains the NSGA-II backbone [6] and introduces warm-start sampling and repair projection before objective evaluation. Warm-start sampling seeds a near-feasible initial population; repair projection is applied after every variation step.

Algorithm 1 EPG-NSGA-II

Input: D, bounds, ratio band, reverse-power parameters, N, G. Output: feasible nondominated set A. 1: P ← Warm-start sampling(D, N) 2: P ← Repair projection(P) 3: Evaluate f1 and f2 for all individuals in P 4: for t = 1 to G do 5: Q ← Variation(P) 6: Q ← Repair projection(Q) 7: Evaluate f1 and f2 for all individuals in Q 8: U ← P ∪ Q 9: P ← nondominated sort + crowding select (U, N) 10: end for 11: A ← feasible nondominated individuals in P 12: return A

WarmStartSampling samples ratios within engineering bounds, projects the aggregate ratio into the planning band, and allocates storage to stations with higher reverse-power pressure.

RepairProjection clips variables, repairs the aggregate-ratio band, checks station-level and upstream reverse-power constraints, and performs a final feasibility check.

III.  EXPERIMENTS

A.  Setup

The benchmark is a public-data-informed synthetic county constructed from scaled IEEE 33-bus feeders [7] and PVGIS irradiance [8]. We test four county sizes, K=10, 20, 30, and 40, with population 100 and three seeds per setting. Plain NSGA-II is run for 800 generations as a longer-budget reference, while EPG-NSGA-II is run for 400 generations.

B.  Efficiency and Ablation

TABLE I. NORMALIZED HYPERVOLUME RESULTS

| Method | K=10 | K=20 | K=30 | K=40 |
| --- | --- | --- | --- | --- |
| EPG-NSGA-II | 1.000 | 1.000 | 1.000 | 1.000 |
| Repair-only | 0.997 | 0.998 | 0.999 | 1.000 |
| NSGA-II | 0.993 | 0.993 | 0.991 | 0.954 |

Table I reports normalized converged HV across county sizes. Repair-only remains within 0.3% of the full method, suggesting that repair projection is important for converged quality in this setting. Plain NSGA-II shows a larger gap as K grows, reaching 4.6% at K=40.

At K=40, EPG-NSGA-II reaches a comparable HV with fewer generations under the fixed-population setting.

C.  County-Level Application at K=20

At K=20, the knee solution has a regional capacity-load ratio of 1.80, an annualized cost index equivalent to 188.82 million CNY/yr, and EENS of 114 MWh/yr. PV-heavy stations receive storage, while low-ratio stations rely more on tie-line support (Fig. 1). Relative to the uniform R=2.0 baseline, the elastic configuration reduces the annualized cost index by 13.1% under equal EENS in this synthetic case.

Fig. 1.  Elastic planning configuration for the synthetic county case.

IV.  CONCLUSION

EPG-NSGA-II combines feasibility-aware initialization and repair projection for elastic capacity-load ratio planning under high PV penetration. The synthetic cases show a lower cost index under equal EENS and improved search efficiency compared with plain NSGA-II. Future work will consider real-grid calibration, energy-limited storage, and statistical testing.

REFERENCES

[1]  J. Xiao, R. Liu, and M. Long, "Relationship between substation capacity-load ratio and the next-level medium-voltage distribution network," Electric Power Construction, vol. 36, no. 11, pp. 45-50, 2015 (in Chinese).

[2]  K. Wang, Z. He, J. Ye, Y. Lin, and Y. Ma, "Capacity-load-ratio optimal configuration for coordinated planning of multi-voltage-level grids," Southern Power System Technology, vol. 19, no. 7, pp. 131-139, 2025 (in Chinese).

[3]  Q. Hou, N. Zhang, E. Du, M. Miao, F. Peng, and C. Kang, "Probabilistic duck curve in high PV penetration power system," Applied Energy, 2019.

[4]  T. Lin, G. Wu, S. Lai, H. Hu, and Z. Hu, "Calculation of distribution network PV hosting capacity considering source-load uncertainty and active management," Electronics, vol. 13, art. 4048, 2024.

[5]  M. Nicolini, "Multi-objective genetic algorithms in designing redundant water distribution systems," in Proc. 2025 IEEE Int. Conf. MIND, 2025.

[6]  K. Deb, A. Pratap, S. Agarwal, and T. Meyarivan, "A fast and elitist multiobjective genetic algorithm: NSGA-II," IEEE Trans. Evol. Comput., vol. 6, no. 2, pp. 182-197, 2002.

[7]  M. E. Baran and F. F. Wu, "Network reconfiguration in distribution systems for loss reduction and load balancing," IEEE Trans. Power Del., vol. 4, no. 2, pp. 1401-1407, 1989.

[8] European Commission, Joint Research Centre, “JRC Photovoltaic Geographical Information System (PVGIS),” [Online]. Available: https://re.jrc.ec.europa.eu/pvg_tools/en/. [Accessed: Jul. 6, 2026].