## Slide 1
MIND 2026
ENGINEERING-PRIOR-GUIDED OPTIMIZATION
EPG-NSGA-II
Engineering-Prior-Guided NSGA-II for Differentiated Capacity-Load Ratio Optimization in County-Level 110 kV Grids with High Distributed PV Penetration
Dunbin Xu · Ke Wang · Yan Xu* · Ziyue Huang · Fei Geng · Rui Yuan
State Grid Xuzhou Power Supply Company
State Grid Jiangsu Electric Power Design & Consulting Co., Ltd. Xuzhou Survey and Design Branch
GRAPHICAL ABSTRACT
PV-rich 110 kV substations
Seeding + feasibility repair
Engineering priors enter the search
R1
P1
R2
P2
Rj
Pj
Differentiated CLR + storage
* Corresponding author: Yan Xu
01 / 05
Notes: Hello everyone. Today I will present Engineering-Prior-Guided NSGA-II, or EPG-NSGA-II, for differentiated capacity-load ratio optimization in county-level 110-kilovolt grids with high distributed photovoltaic penetration. This work jointly plans transformer capacity and storage power. I will briefly explain the planning problem, our algorithm, and the main experimental results.

## Slide 2
01 / BACKGROUND & PROBLEM
High PV calls for differentiated planning
a Reverse-flow coupling and planning model
b Station heterogeneity | K = 20
Upstream grid
Midday PV export Reverse flow
Distributed PV
Local load
110 kV substation
Decisions: CLR Rj and storage power Pj (MW)
CLR = transformer capacity / forecast peak load
Minimize annualized cost and EENS
million CNY/yr · MWh/yr · N−1 supply inadequacy
Selected CLR
3.0
2.4
1.8
1.2
1.7
2.0
2.5
3.0
3.6
Source-load ratio
2.0 cap reference
20 stations · Selected CLR 1.55–2.64
Source-load ratio = installed PV capacity / current peak load
Constraints: station reverse flow · aggregate CLR band · optional upstream reverse-flow limit
Source: camera-ready paper, Sections I–II and Fig. 1. Public-data benchmark; all 20 station records shown.
02 / 05
Notes: High distributed PV penetration changes power flow. Electricity normally moves from the upstream grid toward local demand, but midday PV generation can create reverse flow through a substation. The planning challenge is that substations differ in PV penetration and transfer capability, while a fixed capacity-load ratio cap of two treats these differences uniformly.
We therefore optimize two quantities at each station: its capacity-load ratio, or CLR, and its storage power rating in megawatts. CLR is dimensionless and means planned transformer capacity divided by forecast peak load. The paper uses a five-year forecast with five percent annual growth.
The scatter shows all twenty stations in the reported design, with selected CLRs from one point five five to two point six four. Its source-load ratio divides installed PV capacity by current peak load. The dashed line marks the two-point-zero comparison cap.
The objectives are annualized cost, in million yuan per year, and expected energy not supplied, or EENS, in megawatt-hours per year. EENS measures supply inadequacy under N-minus-one contingencies. Feasibility is defined by station reverse-flow limits, an aggregate CLR band from one point eight to three, and an upstream reverse-flow limit when enabled.

## Slide 3
02 / PROPOSED SOLUTION
Engineering priors guide the search
Standard NSGA-II + engineering-prior seeding + feasibility repair
Seed & repair
Evaluate
Select
Vary + repair
Sample CLR Start storage at zero
Cost · EENS · Constraints
Non-dominated ranking
Repair every offspring
Repeated evolutionary search
ENGINEERING-PRIOR REPAIR
1 Aggregate CLR
2 Station reverse flow
3 Upstream limit
Bounded common offset
Increase storage power
Greedy allocation when enabled
β = 0.85
Residual violations: constraint domination. Standard variation and environmental selection are retained.
Source: Section II-B, Algorithm 1. r0: pre-storage reverse injection; Lp: forecast peak load; Pmax: storage rating bound.
03 / 05
Notes: Our solution adds engineering-prior seeding and feasibility repair to standard NSGA-II. The key change is how candidate plans are constructed and adjusted.
For the initial population, we sample station CLR values, start storage power at zero, and apply repair before evaluation. During evolution, standard variation produces offspring, the same repair adjusts them, and evaluation and selection form the next generation.
Repair has three priorities. First, a bounded common offset shifts station CLR values to satisfy the load-weighted aggregate band. Second, station-level repair increases storage power where residual reverse injection exceeds the transformer reverse-loading limit. Third, when the upstream constraint is enabled, storage is allocated in descending order of residual reverse injection, until the upstream limit is met or adjustable storage ratings reach their bounds.
Any remaining infeasibility is handled by constraint domination. Standard variation, non-dominated ranking, and environmental selection are retained. These engineering rules direct candidate construction toward feasibility while the evolutionary search explores the cost and adequacy trade-off.

## Slide 4
03 / EXPERIMENTAL EVIDENCE
Better search, lower modeled planning cost
Mean final HV | K = 40
+4.8%
EPG: 400 gen · NSGA-II: 800 gen
Annualized cost | K = 20
−3.4%
236.40 → 228.43 million CNY/yr
Modeled EENS | K = 20
0.00
561.00 → 0.00 MWh/yr
a Search dynamics | K = 40
b Ablation | K = 40
1.1
1.0
0.5
0.0
0
200
400
600
800
Generation
Normalized HV
84
generations
EPG-NSGA-II
NSGA-II
Mean ± 1 SD · n = 3 runs
NSGA-II
NSGA-III
Seeding-only
Repair-only
EPG-NSGA-II
1.000
0.985
0.998
1.048
1.048
0.96
1.00
1.04
1.07
Final normalized HV
○ run · | mean
Population 100 · Three independent runs · HV normalized to NSGA-II final mean · Common reference point
Table I / Section III. Public-data model; storage energy/SOC limits and real-grid calibration remain future work.
04 / 05
Notes: The experiments use a public-data benchmark, with loads scaled from the IEEE thirty-three-bus system and PV profiles derived from PVGIS. Population size is one hundred, and results are averaged over three independent runs.
For forty substations, EPG-NSGA-II achieves four point eight percent higher mean final hypervolume than standard NSGA-II. The left panel shows convergence, with shading indicating one standard deviation across the three runs. Hypervolume is normalized to the standard baseline's final mean using a common reference point. The baselines run for eight hundred generations, while EPG-NSGA-II and its ablations run for four hundred. The mean EPG curve reaches the standard baseline's final hypervolume by generation eighty-four. The right panel shows every final run and its method mean. Repair-only nearly matches the full method, while seeding-only remains close to the baseline. Repair is therefore the main contributor to the final gain.
The twenty-substation planning comparison is summarized above the plots. Annualized cost falls from two hundred thirty-six point four zero to two hundred twenty-eight point four three million yuan per year, a reduction of three point four percent. Modeled EENS falls from five hundred sixty-one to zero megawatt-hours per year relative to the two-point-zero-capped design.
These results apply to the current model. Storage energy and state-of-charge limits, together with real-grid calibration, remain future work.

## Slide 5
MIND 2026
EPG-NSGA-II
Thank you
Questions & discussion
R1,P1
R2,P2
Rj,Pj
Engineering priors support more effective search and differentiated CLR and storage planning.
ENGINEERING KNOWLEDGE → CANDIDATE CONSTRUCTION → PLANNING TRADE-OFFS
Engineering-Prior-Guided NSGA-II · County-level 110 kV planning
05 / 05
Notes: The main takeaway is that engineering-prior seeding and repair support more effective constrained search and differentiated CLR and storage planning. Thank you for your attention. I welcome your questions.