## Slide 1
MIND 2026
EVOLUTIONARY MULTIOBJECTIVE OPTIMIZATION
EPG-NSGA-II
Engineering-Prior-Guided NSGA-II for Differentiated Capacity-Load Ratio Optimization in County-Level 110 kV Grids with High Distributed PV Penetration
Dunbin Xu · Ke Wang · Yan Xu* · Ziyue Huang · Fei Geng · Rui Yuan
* Corresponding author
State Grid Xuzhou Power Supply Company
State Grid Jiangsu Electric Power Design & Consulting Co., Ltd., Xuzhou Survey and Design Branch
ENGINEERING PRIORS FOR DIFFERENTIATED GRID PLANNING
01 / 05
Notes: Hello everyone. Today I will present Engineering-Prior-Guided NSGA-II, or EPG-NSGA-II, for differentiated capacity-load ratio optimization in county-level 110-kilovolt grids with high distributed photovoltaic penetration. This work jointly plans transformer capacity and storage power. I will briefly explain the planning problem, our algorithm, and the main experimental results.

## Slide 2
High PV calls for differentiated planning
A fixed CLR cap of 2.0 misses station-level PV and transfer differences.
Upstream grid
Station j
110 kV substation
Distributed PV
Local load
Midday export Reverse flow
JOINT STATION DECISIONS
CLR Rj · Storage Pj (MW)
CLR = planned transformer capacity divided by forecast peak load
MINIMIZE
Annualized cost
million CNY/yr
Expected energy not supplied
EENS · MWh/yr · N−1 inadequacy
Feasibility: station reverse-flow limits · aggregate CLR band 1.80–3.00
Upstream reverse-flow limit included when enabled
Source: camera-ready paper, Introduction and Section II-A. CLR is dimensionless.
02 / 05
Notes: High distributed PV penetration changes power flow. Electricity normally moves from the upstream grid toward local demand, but midday PV generation can create reverse flow through a substation. The planning challenge is that substations differ in PV penetration and transfer capability, while a fixed capacity-load ratio cap of two treats these differences uniformly.
We therefore optimize two quantities at each station: its capacity-load ratio, or CLR, and its storage power rating in megawatts. CLR is dimensionless and means planned transformer capacity divided by forecast peak load. The paper uses a five-year forecast with five percent annual growth.
The objectives are annualized cost, in million yuan per year, and expected energy not supplied, or EENS, in megawatt-hours per year. EENS measures supply inadequacy under N-minus-one contingencies. Feasibility is defined by station reverse-flow limits, an aggregate CLR band from one point eight to three, and an upstream reverse-flow limit when enabled.

## Slide 3
Engineering priors guide the search
Standard NSGA-II + seeding + feasibility repair
Seed & repair
Initial population
Variation
Standard operators
Repair
After variation
Evaluate & select
Cost, EENS, feasibility
Next generation: return to variation
REPAIR PRIORITIES
1 Aggregate CLR
2 Station reverse flow
3 Upstream flow
Bounded common offset
Increase storage power
Allocate storage, if enabled
Remaining violations use constraint domination; standard ranking and selection are retained.
Source: camera-ready paper, Section II-B and Algorithm 1.
03 / 05
Notes: Our solution adds engineering-prior seeding and feasibility repair to standard NSGA-II. The key change is how candidate plans are constructed and adjusted.
For the initial population, we sample station CLR values, start storage power at zero, and apply repair before evaluation. During evolution, standard variation produces offspring, the same repair adjusts them, and evaluation and selection form the next generation.
Repair has three priorities. First, a bounded common offset shifts station CLR values to satisfy the load-weighted aggregate band. Second, station-level repair increases storage power where residual reverse injection exceeds the transformer reverse-loading limit. Third, when the upstream constraint is enabled, storage is allocated in descending order of residual reverse injection, until the upstream limit is met or adjustable storage ratings reach their bounds.
Any remaining infeasibility is handled by constraint domination. Standard variation, non-dominated ranking, and environmental selection are retained. These engineering rules direct candidate construction toward feasibility while the evolutionary search explores the cost and adequacy trade-off.

## Slide 4
Better search, lower modeled planning cost
Search quality | K = 40
+4.8%
vs standard NSGA-II mean final hypervolume
Planning outcome | K = 20
−3.4%
annualized cost
Method | HV | Gen.
NSGA-II | 1.000 | 800
NSGA-III | 0.985 | 800
Seeding-only | 0.998 | 400
Repair-only | 1.048 | 400
EPG-NSGA-II | 1.048 | 400
Annualized cost (million CNY/yr)
236.40
→
228.43
Modeled EENS (MWh/yr)
561.00
→
0.00
HV normalized to NSGA-II at termination; common reference point.
Population 100 · Three independent runs · Repair nearly matches the full method.
2.0-capped → elastic CLR design
Public-data benchmark · Energy/SOC limits and real-grid calibration remain future work.
Source: camera-ready paper, Table I and Section III-C. Values checked against archived experimental CSVs.
04 / 05
Notes: The experiments use a public-data benchmark, with loads scaled from the IEEE thirty-three-bus system and PV profiles derived from PVGIS. Population size is one hundred, and results are averaged over three independent runs.
On the left, for forty substations, EPG-NSGA-II achieves four point eight percent higher mean final hypervolume than standard NSGA-II. Hypervolume is normalized to the standard baseline at termination using a common reference point. The baselines run for eight hundred generations, while EPG-NSGA-II and its ablations run for four hundred. Repair-only nearly matches the full method, while seeding-only remains close to the baseline. Repair is therefore the main contributor to the final gain. The paper also reports that the mean EPG curve reaches the standard baseline's final hypervolume by generation eighty-four.
On the right, the twenty-substation design comparison reduces annualized cost from two hundred thirty-six point four zero to two hundred twenty-eight point four three million yuan per year, a reduction of three point four percent. Modeled EENS falls from five hundred sixty-one to zero megawatt-hours per year relative to the two-point-zero-capped design.
These results apply to the current model. Storage energy and state-of-charge limits, together with real-grid calibration, remain future work.

## Slide 5
MIND 2026
EPG-NSGA-II
Thank you
Questions & discussion
Engineering priors → more effective search → differentiated CLR and storage planning
ENGINEERING PRIORS FOR DIFFERENTIATED GRID PLANNING
05 / 05
Notes: The main takeaway is that engineering-prior seeding and repair support more effective constrained search and differentiated CLR and storage planning. Thank you for your attention. I welcome your questions.